## Legend
FLEXCCSPARAMETERS |  |  |  |  | This section tests different parameter values in IECM to model flexible CCS
| This sheet has all of the needed flexible CCS parameters for bituminous & subbituminous fuel at 3 different plant efficiencies |  |  |  | operations while discharging stored lean solvent. These values are then used in IECM
| Plant efficiencies are implemented in IECM through selection of subcritical, supercritical, or ultra-supercritical plant. |  |  |  | to generate the 'CCS, Discharging Stored Lean Solvent' plant in blue area at left.
| All plants are equipped with: |  |  | In-Furnace NOx Controls
|  |  |  | Hot-Side SCR |  | Field | Fuel Type | Coal Plant Type | Default Value | Flex CCS Value
|  |  |  | Cold-Side ESP |  | Performance, Amine Scrubber Power Req | Subbit | Subcritical | 10.55 | 2.11
|  |  |  | Wet FGD |  | T&S Config, CO2 Unit Compression Energy | Subbit | Subcritical | 84.38 | 16.876
|  |  |  | Carbon Injection |  | Performance, Amine Scrubber Power Req | Subbit | Supercritical | 9.707 | 1.9414
|  |  |  | Once-Through Cooling |  | T&S Config, CO2 Unit Compression Energy | Subbit | Supercritical | 84.38 | 16.876
| All plants pre-CCS have a gross output of 650 MW. |  |  |  |  | Performance, Amine Scrubber Power Req | Subbit | Ultra-supercritical | 8.672 | 1.7344
| Subbituminous fuel is Wyoming PRB; bituminous is Illinois #6. |  |  |  |  | T&S Config, CO2 Unit Compression Energy | Subbit | Ultra-supercritical | 84.38 | 16.876
| Each sheet includes parameters for base plant, plant w/ CCS, and plant w/ flexible CCS when it's dischargin lean solvent. |  |  |  |  | Performance, Amine Scrubber Power Req | Bit | Subcritical | 9.522 | 1.9044
| The CO2 capture system parameters used to create a plant that mimics flex CCS operations when discharing |  |  |  |  | T&S Config, CO2 Unit Compression Energy | Bit | Subcritical | 84.38 | 16.876
|  | stored lean solvent are shown to right in the green box. |  |  |  | Performance, Amine Scrubber Power Req | Bit | Supercritical | 8.785 | 1.757
|  | Note that the Regenerator Heat Requirement (under Capture tab) is always set to 1E-2. |  |  |  | T&S Config, CO2 Unit Compression Energy | Bit | Supercritical | 84.38 | 16.876
|  | The two parameters at right are varied such that the 'Flex CO2 Capture System Use' - that is, |  |  |  | Performance, Amine Scrubber Power Req | Bit | Ultra-supercritical | 7.862 | 1.5724
|  |  | the energy used by the co2 capture system when discharing lean solvent - equals 10% |  |  | T&S Config, CO2 Unit Compression Energy | Bit | Ultra-supercritical | 84.38 | 16.876
of the original CO2 capture system use, as during discharge of stored lean solvent,
all but 10% of the load of the CO2 capture system is eliminated.
IECM files available at: C:\Users\mcraig10\Desktop\EPP Research\Flexible CCS Excel Model\IECMFiles.sdb
ParameterEstimation650MWPlant
This sheet estimates the parameters necessary to model flexible CCS using IECM results for a 650 MW gross (pre-CCS) plant.
Includes results for coal-fired power plant burning bituminous or sub-bituminous coal.
Based on Haibo's calculations provided in earlier iteration of spreadsheet (see sheet 'OLD DO NOT USE')
NumericExample650MW
Two numeric examples comparing operations with flexible CCS versus non-flexible CCS>
One example is done using data provided by the IECM for hypothetical plant.
The other example uses the modeling setup that I use for flexible CCS.
This sheet accounts for additional solvent that must be continuously regenerated to capture CO2 from the fuel burned for the energy used to store lean solvent. Does so using manual iterations.
NumericExample650MWVent
This sheet is same as prior sheet with two exceptions. First, calculates amount of solvent necessary to capture CO2 form fuel used to store lean solvent using ratio calcultaed in ParameterEstimation page.
Second, assumes fuel input is contsant across hours, meaning that when charging stored lean solvent, some fuel is burned from which CO2 is not captured; that CO2 is vented.
NumericExample650MWAbsorber
This sheet is the same as prior sheet, but accounts for the fact that the absorber does not need to be run for lean solvent that is stored.
This means that the parasitic load of the CO2 capture system is a little lower than in the prior sheet; I adjust the CO2 capture system load to account for this lower absorbe rpower demand.
In general, find that absorber load change is negligible; results in 3 MW increase from 455 MW to grid.
This is good, because can't model varying HR anyways.
ExAsModeledInPLEXOS
Under construction - ignore this sheet
NumericExampleV2DiffTankSize
Repeats calculations that are in NumericExampleV2, but using a different lean and rich solvent tank size (for stored solvent).
Purpose of the sheet is to see if the parameter in below cell changes w/ different tank size (IT DOES NOT).
Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to Capture Sys for Stored Lean Solvent (MWh/MWh)
These sheets are then repeated using a 450 MW gross (pre-CCS) plant to see what parameters change for a lower gross plant size.
Answer: the constants that I care about DO NOT change at different gross plant sizes.

## FLEXCCSPARAMETERS
Fuel Type | Coal Plant Type | CCS Configuration | Fuel Input (tons/hr) | Gross Output (MW) | Net Output (MW) | CO2 Capture System Use (MW) | Solvent Flow Rate (tons/hr) | Gross HR (Btu/kWh) | Net HR (Btu/kWh) | CCS Net HR Penalty (%) | CCS Net Capacity Penalty (%) | CCS Net Capacity Penalty (MW) | Regenerator Size (MW) | Solvent Flow/E to CO2Cap+Regen (ton/MWh) | Net E to Grid When Discharging Stored Lean/Ton Stored Lean Solvent Discharged (MWh/ton) | Gross HR (tons/MWh) | Tons Fuel Input/Ton Solvent Regenerated (MMBtu/ton) | Tons Solvent/Ton Fuel Burned (ton/MMBtu) | E for Solvent to Capture CO2 from Fuel for To-Be-Stored Lean/E to Store Lean Solvent (MWh/MWh) | E to Regenerator/E to CO2Cap (MWh/MWh) | Net E to Grid / E to CO2 Cap+Regen (MWh/MWh) | Net E to Grid When Discharging Stored Lean/E Used to Store Lean Solvent (MWh/MWh)
Subbituminous | Subcritical | Base | 354.2 | 650 | 602.5 | 0 | 0 | 9090 | 9807 | 0% | 0%
Subbituminous | Subcritical | CCS | 354.2 | 517.1 | 411.4 | 54.55 | 8624 | 11430 | 14360 | 46.43% | -31.72% | 191.1 | 136.55 | 45.1282 |  | 0.54188 | 0.012008 | 24.3478 |  | 2.5032 | 2.1528
Subbituminous | Subcritical | Flex CCS | 354.2 | 650 | 577.5 | 13.71 | 8625 | 9090 | 10230 | 4.313% | -4.149% |  |  |  | 0.066957 |  |  |  | 0.41314 |  |  | 3.0216
Subbituminous | Supercritical | Base | 334.6 | 650 | 605.3 | 0 | 0 | 8588 | 9222 | 0% | 0%
Subbituminous | Supercritical | CCS | 334.6 | 530.8 | 431.5 | 51.53 | 8147 | 10510 | 12930 | 40.21% | -28.71% | 173.8 | 122.27 | 46.8757 |  | 0.51235 | 0.01093 | 24.3485 |  | 2.3728 | 2.4827
Subbituminous | Supercritical | Flex CCS | 334.6 | 650 | 583.5 | 12.61 | 8147 | 8588 | 9567 | 3.741% | -3.602% |  |  |  | 0.071621 |  |  |  | 0.36263 |  |  | 3.3573
Subbituminous | Ultra-supercritical | Base | 304.9 | 650 | 609 | 0 | 0 | 7825 | 8352 | 0% | 0%
Subbituminous | Ultra-supercritical | CCS | 304.9 | 541.4 | 450.2 | 46.95 | 7423 | 9393 | 11300 | 35.3% | -26.08% | 158.8 | 111.85 | 46.7443 |  | 0.46674 | 0.009985 | 24.3457 |  | 2.3823 | 2.835
Subbituminous | Ultra-supercritical | Flex CCS | 304.9 | 650 | 589.3 | 11.24 | 7424 | 7825 | 8631 | 3.341% | -3.235% |  |  |  | 0.079378 |  |  |  | 0.32116 |  |  | 3.7105
Bituminous | Subcritical | Base | 244.1 | 650 | 609.4 | 0 | 0 | 8763 | 9348 | 0% | 0%
Bituminous | Subcritical | CCS | 244.1 | 527.8 | 431 | 50.26 | 7944 | 10800 | 13220 | 41.42% | -29.27% | 178.4 | 128.14 | 44.5291 |  | 0.37214 | 0.0083572 | 32.544 |  | 2.5495 | 2.4159
Bituminous | Subcritical | Flex CCS | 244.1 | 650 | 585.4 | 12.35 | 7941 | 8763 | 9730 | 4.086% | -3.938% |  |  |  | 0.073719 |  |  |  | 0.37358 |  |  | 3.2826
Bituminous | Supercritical | Base | 230.5 | 650 | 611.8 | 0 | 0 | 8279 | 8796 | 0% | 0%
Bituminous | Supercritical | CCS | 230.5 | 540.2 | 449.4 | 47.46 | 7501 | 9960 | 11970 | 36.08% | -26.54% | 162.4 | 114.94 | 46.1884 |  | 0.35183 | 0.0076173 | 32.5423 |  | 2.4218 | 2.7672
Bituminous | Supercritical | Flex CCS | 230.6 | 650 | 590.7 | 11.42 | 7502 | 8279 | 9110 | 3.57% | -3.449% |  |  |  | 0.078739 |  |  |  | 0.32959 |  |  | 3.6368
Bituminous | Ultra-supercritical | Base | 210.1 | 650 | 614.8 | 0 | 0 | 7543 | 7974 | 0% | 0%
Bituminous | Ultra-supercritical | CCS | 210.1 | 550 | 466.6 | 43.24 | 6835 | 8914 | 10510 | 31.8% | -24.11% | 148.2 | 104.96 | 46.1201 |  | 0.32078 | 0.0069554 | 32.5321 |  | 2.4274 | 3.1484
Bituminous | Ultra-supercritical | Flex CCS | 210.1 | 650 | 595.8 | 10.2 | 6835 | 7543 | 8229 | 3.198% | -3.09% |  |  |  | 0.087169 |  |  |  | 0.29245 |  |  | 4.0202
PARAMETER VALUES FOR MATLAB
Fuel Type | Coal Plant Type | E for Solvent to Capture CO2 from Fuel for To-Be-Stored Lean/E to Store Lean Solvent (MWh/MWh) | E to Regenerator/E to CO2Cap (MWh/MWh) | Net E to Grid / E to CO2 Cap+Regen (MWh/MWh) | Net E to Grid When Discharging Stored Lean/E Used to Store Lean Solvent (MWh/MWh) | CCS Net HR (Btu/kWh) | Base Plant Net HR (Btu/kWh) | CCS Net HR Penalty (%) | CCS Net Capacity Penalty (%) | CCS w/ Discharged Stored Lean Solvent Net HR Penalty (%) | CCS w/ Discharged Stored Lean Solvent Capacity Penalty (%)
Subbituminous | Subcritical | 0.41314 | 2.5032 | 2.1528 | 3.0216 | 14360 | 9807 | 46.43% | -31.72% | 4.313% | -4.149%
Subbituminous | Supercritical | 0.36263 | 2.3728 | 2.4827 | 3.3573 | 12930 | 9222 | 40.21% | -28.71% | 3.741% | -3.602%
Subbituminous | Ultra-supercritical | 0.32116 | 2.3823 | 2.835 | 3.7105 | 11300 | 8352 | 35.3% | -26.08% | 3.341% | -3.235%
Bituminous | Subcritical | 0.37358 | 2.5495 | 2.4159 | 3.2826 | 13220 | 9348 | 41.42% | -29.27% | 4.086% | -3.938%
Bituminous | Supercritical | 0.32959 | 2.4218 | 2.7672 | 3.6368 | 11970 | 8796 | 36.08% | -26.54% | 3.57% | -3.449%
Bituminous | Ultra-supercritical | 0.29245 | 2.4274 | 3.1484 | 4.0202 | 10510 | 7974 | 31.8% | -24.11% | 3.198% | -3.09%

## ParameterEstimation650MWPlant
Determining parameters for base CCS facility and flexible CCS facility using IECM results for a 650 MW gross plant | [7 empty] | This section tests different parameter values in IECM to model flexible CCS
burning sub-bit. or bit. fuel and at constant fuel input. | [7 empty] | operations while discharging stored lean solvent. These values are then used in IECM
BASE PLANT |  | CCS Plant | [5 empty] | to generate the 'CCS, Discharging Stored Lean Solvent' plant in blue area at left. |  |  |  |  | TESTING RELATIONSHIP BETWEEN CO2 CAPTURE SYSTEM USE AND REGENERATOR USE (ALL IN MW)
Control techs: |  | Same as base plant plus amine system | [7 empty] | TESTING SOLVENT STORAGE DISCHARGING |  |  | I want to know what the relationship in energy demanded by the regenerator and the rest of the CO2 capture system is.
In-Furnace NOx Controls | [9 empty] | For plant w/ CCS @ 650 MW gross output & bituminous fuel |  |  | The rest of the CO2 capture system's energy use is available in the CO2 Capture System Use field, already provided in MW.
Hot-Side SCR |  | CCS Plant w/ Solvent Storage | [7 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | The regenerator energy demand, in MWh, can be determined by taking the difference in the net output of a coal plant
Cold-Side ESP |  | Model as CCS plant while discharging stored lean solvent. | [7 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | w/out and w/ CCS (which embodies the entire energy demand by capturing CO2) and subtracting the CO2 Capture System Use
Wet FGD |  | See tables at right for parameter values to model generation while discharging | [7 empty] | Capture, Regen. Heat Requirement | 1523 | 0.01 | value.
Carbon Injection |  |  | stored lean solvent. | [6 empty] | Performance, Amine Scrubber Power Req | 7.159 | 0.7
Once-Through Cooling | [12 empty] | Data is for base vs. CCS plant, defined at left, with bituminous coal.
Boiler Efficiency: 89.64% (default) | [9 empty] | For plant w/ CCS @ 650 MW gross output & subbituminous fuel
Coal type: | [9 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | Base Plant Gross Output (MW) | Base Plant Net Output (MW) | Base Plant Fuel Input (tons/hr) | CCS Plant Fuel Input (tons/hr) | CCS Plant Gross Output (MW) | CCS Plant Net Output (MW) | CCS Plant CO2 Capture System Use (MW) | Base-CCS Net Output (MW) | CCS Plant Implied Regenerator Energy Use (MW) | Regenerator Energy Use / CO2 Capture System Use (MW/MW)
Subbit: Wyoming PRB | [9 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | 650 | 613.7 | 203.4 | 203.4 | 514.4 | 455 | 46.53 | 158.7 | 112.17 | 2.4107
Bit: Appalachian Low-Sulfur | [9 empty] | Capture, Regen. Heat Requirement | 1514 | 0.01 | 500 | 471.9 | 156.5 | 156.5 | 416.4 | 349.7 | 35.79 | 122.2 | 86.41 | 2.4144
[10 empty] | Performance, Amine Scrubber Power Req | 7.928 | 0.8 | 400 | 377.3 | 125.2 | 125.2 | 333.1 | 279.6 | 28.63 | 97.7 | 69.07 | 2.4125
Plant | Fuel Input (tons/hr) | Gross Output (MW) | Net Output (MW) | CO2 Capture System Use (MW) | Solvent Flow Rate (tons/hr) | [15 empty] | Mean: | 2.4125
Subbituminous Coal
Base | 334.6 | 650 | 605.3 | 0 | 0 | Capac Pen, Base -> CCS (%)
CCS | 334.6 | 530.8 | 431.5 | 51.53 | 8147 | 0.28713
CCS, Discharging Stored Lean Solvent | 334.6 | 650 | 590.9 | 5.2 | 8147
Bituminous Coal
Base | 203.4 | 650 | 613.7 | 0 | 0
CCS | 203.4 | 541.4 | 455 | 46.53 | 7431 | 0.2586 | Capac Pen, Base -> CCS (%)
CCS, Discharging Stored Lean Solvent | 203.4 | 650 | 601.4 | 4.55 | 7431 | 8.7 | Pre-CCS Net Heat Rate (MMBtu/MWh)
[6 empty] | 8.2 | Pre-CCS Gross Heat Rate (MMBtu/MWh)
Parameter Estimates | [5 empty] | 11.7 | CCS Net Heat Rate (MMBtu/MWh)
Value | Units | Parameter |  |  |  | 9.8 | CCS Gross Heat Rate (MMBtu/MWh)
Subbituminous Coal | [5 empty] | 0.34483 | Heat Rate Penalty (%)
Continuous (Normal) CCS Operations
173.8 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
46.8757 | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
0.052964 | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
2.4827 | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator) [constant 'd' in slide 9 on accompanying slide deck]
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
122.27 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
66.6312 | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS Operations While Discharging Stored Lean Solvent
0.07253 | MWh/tons | Incremental net energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent used.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
3.3999 | MWh/MWh | Incremental net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
[Constant 'Y' on slide 17 in accompanying slide deck]
0.56625 | tons/MWh | Net Heat Rate = Fuel In / Net Grid Output
Value | Units | Parameter
Bituminous Coal
Continuous (Normal) CCS Operations
158.7 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
46.8242 | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
0.06123 | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
2.867 | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator) [constant 'd' in slide 9 on accompanying slide deck]
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
112.17 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
66.2477 | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS Operations While Discharging Stored Lean Solvent
0.080931 | MWh/tons | Incremental et energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent discharged.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
3.7895 | MWh/MWh | Net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
Know that for every ton stored lean solvent discharged, can generate 0.07 MWh.
[Constant 'Y' on slide 17 in accompanying slide deck]
0.33821 | tons/MWh | Net Heat Rate = Fuel In / Net Grid Output
0.89721
Determining Extra Solvent Needed to Capture CO2 from Fuel Used to Regenerate Stored Lean Solvent
0.33143 | tons fuel / MWh | Gross Heat Rate = Fuel In / (Gross Output) = Fuel In / (Pgrid + Pco2 + Pregen)
[This includes energy to the regenerator!]
Convert value to tons fuel to provide energy to regenerate solvent / tons solvent using MWh energy input required to regenerate 1 ton of solvent
0.0070782 | tons fuel / ton solvent regenerated
Using that value, know for each ton of to-be-stored lean solvent want to regenerate, how many tons of fuel required
|  | Ex: | 1 | to-be-stored tons of lean solvent
|  |  | 0.0070782 | required tons of fuel
Now need to know additional fuel input to capture CO2 from fuel used to regenerate to-be-stored lean solvent
To know that, need to know how many tons of solvent is required to capture CO2 emissions from some amount of fuel input
36.5339 | tons solvent / ton fuel's co2 emissions |  | [this assumes that part of fuel input is used to generate that lean]
So, need ~24 tons of solvent to capture CO2 emissions from a single ton of fuel input
Now get extra tons of solvent needed per ton of to-be-stored-lean-solvent regenerated - see calculation steps below. Scalar = (X/(1/Z-X)).
0.34879 | ton extra solvent necessary / ton solvent to be stored regenerated |  |  |  | [SEE CALCULATION STEPS BELOW]
And we know how much MWh required to regenerate 1 ton of solvent, so can get a MWh value for that solvent
0.007449 | MWh for extra solvent / ton solvent to be stored regenerated
And I know how much energy it takes to regenerate one ton of to-be-stored solvent, so I can calculate the ratio of MWh for extra solvent to MWh for to-be-stored solvent
0.34879 | MWh for extra solvent / MWh for solvent to be regenerated
[since using same MWh/ton solvent ratio for numerator and denominator, above value is the value as 'ton extra solvent / ton solvent ot be regenerated' value[
CALCULATION STEPS FOR TON EXTRA SOLVENT / TON SOLVENT TO BE STORED REGENERATED
X = tons fuel / ton solvent regenerated
Z = tons solvent / ton fuel's CO2 emissions
A = amount of extra solvent regenerated to capture CO2 emissions from fuel used to regenerate to-be-stored lean solvent
B = amount of to-be-stored lean solvent regenerated
Total Fuel Consumption = X*A + X*B
Only A captures CO2 emissions, not B. So - how much B is necessary to capture CO2?
B*(1/Z) = quantity of fuel from which CO2 emissions are captured by B
Quantity of fuel from which CO2 emissions must be captured is entire fuel input for A and B (since A does not contribute at all to capturing CO2). Thus:
B* (1/Z) = Total Fuel Consumption = X*A + X*B
B*(1/Z-X) = X*A
B=X*A/(1/Z-X)
B=(X/(1/Z-X))*A
So the relevant scalar between extra solvent needed to capture CO2 from fuel used to generate to-be-stored lean solvent is:
X/(1/Z-X))

## NumericExample650MWVent
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  | 4 time steps: | [10 empty] | Same Example Using My Modeling Scheme
During charging, input constant fuel & vent CO2 from that extra fuel. |  |  |  | t=0: max generation | [10 empty] | Base CCS Plant
Plant specification: CCS plant type on prior sheet, bituminous coal |  |  |  | t=1: store lean solvent (fully charge lean solvent tank) | [10 empty] | 455 | Net Capacity w/ CCS (MW) |  |  |  | **Note that these values ARE not the same as numeric value to left because of different storage amounts.
Plant Parameters w/ CCS |  |  |  | t=2: max generation | [10 empty] | 613.7 | Pre-CCS Net Capacity (MW) |  |  |  | **However, if you scale based on energy to continuous solvent regeneration, results are the same.
Value | Ref to Prior Sheet (for reference) |  |  | t=3: max generation utilizing stored lean solvent |  |  |  | t= | 0 | 1 | 2 | 3 |  |  | 11% | Heat Rate Penalty |  |  |  |  | t= | 0 | 1 | 2 | 3
455 | 455 | MW | Net output |  |  |  |  | Non-flexible CCS | [6 empty] | 25.86% | CCS Capacity Penalty |  |  |  |  | Continuous Gen
158.7 | 158.7 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  |  |  |  | Net Power Output to Grid (MW): | 455 | 455 | 455 | 455 |  |  | 14.86% | Regenerator Capacity Penalty |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 455 | 455 | 455
7431 | 7431 | tons | Lean solvent flow rate |  |  |  |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 7431 | 7431 | 7431 |  |  | 46.53 | Max Energy Input to CO2 Capture System (MWh) | [8 empty] | 1820 | Total Gen
46.53 | 46.53 | MW | CO2 Capture System Use |  |  |  |  | CO2 Capture System Power Use (MW): | 46.53 | 46.53 | 46.53 | 46.53 |  |  | 9.7786 | Net Energy to Grid per Energy Input to CO2 Capture System (MWh/MWh) |  |  |  |  | Use of Stored Solvent, True Pump System
112.17 | . | MW | Regenerator Use |  |  |  |  | Regenerator Power Use (MW): | 112.17 | 112.17 | 112.17 | 112.17 |  |  | 20% | Min loading of steam turbine |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 454.7522
0.021356 | 0.021356 | MWh/ton | Energy required per ton solvent regenerated |  |  |  |  | Total Power Input to Capture CO2 (MW): | 158.7 | 158.7 | 158.7 | 158.7 |  |  | 91 | Min load of steam turbine (MW) |  |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 0.025622 | 0 | 0
0.06123 | 0.06123 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  |  |  | Gross Power Output (MW): | 613.7 | 613.7 | 613.7 | 613.7 |  |  | 159.7034 | Tons lean solvent regenerated per unit energy used in CO2 Capture System (tons/MWh) |  |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 46.5044 | 46.53 | 46.5047
0.70681 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator | [8 empty] | 1820 | Total Net Power Delivery to Grid (MW): |  | 1451.801 | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to |  |  |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 46.5047
0.29319 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [8 empty] | 2454.8 | Total Gross Output (MW) |  |  |  | Capture Sys for Stored Lean Solvent (MWh/MWh): |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 37.1984 | 0 | 0
9.7786 | 9.7786 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank | Solvent Storage Generator | [5 empty] | Solvent Regenerated (tons): | 7431 | 7431 | 7431 | 7426.9536
12.1085 | 12.1085 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  |  |  |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 455 | 207.2407 | 455 | 271.3101 | [Declines b/c of less continuous solvent regen] | 0 | General Parameters | [5 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 0.33152
0.33143 | 0.33143 | tons fuel/MWh | Gross Heat Rate |  |  |  |  | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 242.793 | [Based on discharged amount of stored lean solvent] | 601.3983 | 90% | Heat Rate Penalty Reduction |  |  |  |  | Solvent Flow from Stored Lean Solvent (tons): | 0 | 0 | 0 | 4.0964
[8 empty] | Total Net Power Output to Grid (MW): | 455 | 207.2407 | 455 | 514.1031 | [Not at max net output because would need full lean solvent tank to get max; see right] | 601.3983 | 95.75% | Capacity Penalty Reduction |  |  | 12.8844 |  | Percent of Continual Solvent Flow Displaced by Stored Solvent (%): | 0 | 0 | 0 | 0.05513%
Plant Parameters w/ CCS While Discharging Stored Lean Solvent | [7 empty] | Total Mass Solvent Continuously Regenerated (tons): | 7431 | 4431 | 7431 | 4431 | [Limited by absorber capacity] | 0 | 3.7895 | Net energy output to grid per energy pumped (MWh/MWh) |  |  |  |  | Total Max Capacity, Accounting for % Continual Regeneration Displaced (MW): | 0 | 0 | 0 | 455.0838
Value | Ref to Prior Sheet (for reference) | [6 empty] | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 7431 | 3384.6264 | 7431 | 4431 | [Manually calculated through iterative procedure; set value to that in prior row ('Total Mass Solvent Continuously Regenerated'), then subtract value below in 'Required Adder to Continuous Lean Solvent' row iteratively until that value = 1.] | 0 |  | [Includes energy to regenerator in denominator] |  |  |  |  | Total Solvent Flow Rate (tons): | 7431 | 7431 | 7431 | 7431.05
601.4 | 601.4 | MW | Net output |  |  |  |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 1046.3736 | 0 | 0 | [Discharge entire tank] | 7431 | 12.9389 | Net energy output to grid per energy pumped, excluding energy to regenerator in value this is multiplied with (MWh/MWh) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 0.025622
7431 | 7431 | tons | Lean solvent flow rate |  |  |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 3000 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 7431 |  | equals prior parameter*(1+Eregen/Eco2capturesystem) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 0.3059
4.55 | 4.55 | MW | CO2 Capture System Use |  |  |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3000 |  | 7431 | 606.9493 | Max total (Base + SS) achievable capcaity (MW) |  |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 455.0838
0 | . | MW | Regenerator Use |  |  |  |  | Mass of Solvent Passed Through Absorber (tons): | 7431 | 4431 | 7431 | 7431 |  | 0 | [10 empty] | 1456.0838 | Total Gen
3000 | . | tons | Lean and rich solvent tank size |  |  |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 3000 | 0 | 0 | 3000 |  | 0 | I model solvent storage generator as additional stand-alone generator, w/ only incremental generation to base CCS facility. | [9 empty] | -0.19995 | Percent Change in Gen w/ Flex CCS vs. Nonflex CCS
3000 | . | tons | Initial mass of stored rich solvent |  |  |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 3000 | 3000 | 0 |  | 0 | But solvent storage generator really should replace generation from base CCS facility. | [5 empty] | Use of Stored Solvent, Incremental Pump System
0 | . | tons | Initial mass of stored lean solvent |  |  |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 158.6964 | 94.6284 | 158.6964 | 94.6284 |  | 0 | When I have full pump load at my stand alone generator, need to inflate this value to scale from incremental pump system | [5 empty] | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 455
0.021356 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 46.529 | 27.7446 | 46.529 | 27.7446 |  | 0 | to true pump system. | [5 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 0.0064145 | 0 | 0
0.080931 | 0.080931 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 112.1675 | 66.8839 | 112.1675 | 66.8839 |  | 0 | True Pump System | [5 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 46.5044 | 46.53 | 46.53
3.7895 | 3.7895 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  |  |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 6.5518 | 0 | 0 |  |  | 0.025622 | Max Capacity (MW) |  | [Excludes energy to regenerator] |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 46.53
64.068 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 64.068 | 0 | 0 |  | 0 |  | [Steam turbine min load defined as 20%, so must |  |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 37.1984 | 0 | 0
0.33821 | 0.33821 | tons/MWh | Net heat rate |  |  |  |  | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 18.7844 | 0 | 0 |  | 0 |  | maintain 20% load through continuous solvent regeneration.] |  |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 0.082996
[8 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 45.2836 | 0 | 0 |  | 0 | 7499.5898 | Tank size to meet max possible output using stored lean solvent (tons) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 0.0064145
Plant Parameters w/ CCS While Charging Stored Lean Solvent | [7 empty] | CO2 Capture System Power Use, Total (MW): | 46.529 | 46.529 | 46.529 | 27.7446 |  | 0 | 4.092 | Solvent pumped at max pump capacity (tons) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 0.076582
Value | Ref to Prior Sheet (for reference) | [6 empty] | Regenerator Power Use, Total (MW): | 112.1675 | 112.1675 | 112.1675 | 66.8839 |  |  |  |  | [Pump max capacity above does not include energy for regenerator.] |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 455.083
0.34879 | 0.34879 | MWh/MWh | MWh for extra solvent / MWh for solvent to be regenerated |  |  |  |  | Total Power Input to Capture CO2 (MW): | 158.6964 | 158.6964 | 158.6964 | 94.6284 |  |  |  |  | [~80% of tank size can be filled in 1 hour, which makes sense given 20% min load on ST.] | [7 empty] | 1456.083 | Total Gen
0.34879 | 0.34879 | ton solvent/ton solvent | ton extra solvent necessary / ton solvent to be stored regenerated |  |  |  |  | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 613.6964 | 365.9371 | 613.6964 | 608.7316 |  |  | 0.05456% | Percent of solvent necessary for max output that can be stored in 1 hour
0.0070782 | 0.0070782 | ton fuel/ton solvent | tons fuel / ton solvent regenerated (continuously or for storage) |  |  |  |  | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 7430.9556 | 4430.9568 | 7430.9556 | NA
[8 empty] | Required Adder to Continuous Lean Solvent (tons): | -0.044431 | -0.043199 | -0.044431 | NA |  |  | Incremental Pump System | [8 empty] | Use of Stored Solvent w/ Backcalculated Regenerator Energy Use
[8 empty] | Fuel for Net Power Output (tons): | 150.8017 | 68.6863 | 150.8017 | 89.9209 |  |  | 151.9493 | Max incremental generation w/ stored lean solvent (MW) | [7 empty] | Net Energy Output to Grid (MWh): | 455 | 454.9373 | 455 | 455
[8 empty] | Fuel for Continuous Solvent Regen (tons): | 52.5983 | 31.3636 | 52.5983 | 31.3636 |  |  | 1877.5166 | Volume of stored lean solvent for max inc. gen (tons) | [7 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 0.0064145 | 0 | 0 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[8 empty] | Fuel for Stored Solvent Regen (tons): | 0 | 21.2347 | 0 | 0 |  |  | 40.0962 | Max capacity (MW), based on volume of stored lean solven | [7 empty] | Back-calculated Regenerator Energy Use to Store Lean Solvent (MWh): | 0 | 0.061861 | 0 | 0
[8 empty] | Fuel for Discharged Stored Lean Solvent (tons): | 0 | 0 | 0 | 82.1152 |  |  |  |  | necessary for max incremental gen above. | [6 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 46.5236 | 46.53 | 46.53 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[8 empty] | Total Fuel (tons): | 203.4 | 121.2846 | 203.4 | 203.3998 |  |  |  |  | [Includes energy to regenerator.] | [6 empty] | Back-calculated Regenerator Energy Use for Continuous Regeneration (MWh): | 112.3402 | 112.3248 | 112.3402 | 112.3402
[12 empty] | 1879.1031 | Total Net Power Delivery to Grid (MW) |  | 11.7563 | Max capacity (MW), excluding energy to regenerator. | [7 empty] | Tons Lean Solvent Stored (tons): | 0 | 3.197 | 0 | 0
[8 empty] | Fuel for Vented Power Gen (tons): |  | 82.1154 |  | 59.1031 | Change in Net Power Delivery to Grid from Cont. Nonflex CCS ops |  | 0.0064145 | Max capacity (MW), excluding energy to regenerator and accounting for limit on how much true pump system can be filled in 1 hour. | [7 empty] | Tons Solvent Continuously Regenerated (tons): | 7439.1386 | 7438.113 | 7439.1386 | 7439.1386
[8 empty] | CO2 Emissions from Vented Gen (tons): |  | 145.1801 |  | 3.247% | % Change in Net Power Output |  | 3.9944 | Ratio of pump max capacity in incremental vs. true system | [7 empty] | Tons Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3.197
[5 empty] | Tons CO2 Emissions per Ton Wyoming PRB Burned (ton/ton): | 1.768 | [8 empty] | 39.06 | Reduction in base CCS net output per unit energy used to pump lean solvent for storage (MWh/MWh) | [7 empty] | Net Energy to Grid, Tons Continuously Regenerated (MWh): | 455.4985 | 455.4357 | 455.4985 | 455.4985
[8 empty] | Electricity from Extra Fuel (MWh): |  | 247.7593 |  | [= diff in elec gen now & last hr] |  |  | 454.7494 | Max capacity of base CCS facility at max pump capacity (MW) | [7 empty] | Net Energy to Grid, Tons Stored Lean Discharged (MWh): | 0 | 0 | 0 | 0.25874 | 0.25873
[5 empty] | Electricity Price ($/MWh): | 65 |  | Revenues from Electricity ($): |  | 16104.3563 | [5 empty] | Check: should be 20% of capacity of base CCS facility | [8 empty] | 613.8702 | 613.8539 | 613.8702 | 613.8702
[5 empty] | CO2 Price ($/ton): | 10 |  | Cost of Fuel ($): |  | 10740.6999 | [6 empty] | 91 | [6 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 0.25873
[8 empty] | Cost of CO2 Emissions ($): |  | 1451.801 | [13 empty] | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 0.025622
[5 empty] | IECM Delivered Coal Cots ($/ton): | 50 |  | Net Revenues from Vented Gen ($): |  | 3911.8553 | Positive by long shot |  |  |  | Extra Generation Unit | [8 empty] | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 0.23311
[5 empty] | IECM Fuel Heating Value (Btu/lb): | 13080 | [8 empty] | 151.9429 | Max Capacity (MW) | [7 empty] | Total Generation (MWh): | 455 | 454.9309 | 455 | 455.2587
[5 empty] | External Coal Price ($/MMBtu): | 5 | [8 empty] | 23687.3883 | Ratio of generation at extra generating unit to generation at pumping unit (MW/MW) | [11 empty] | 1820.1896 | Total Gen
[5 empty] | Coal Cost using External Coal Price ($/ton): | 130.8 | [assuming 2000 lb/ton]
Lets assume generator fills solvent tank every day (2 hours at full load, so ~14,000 tons).
How much CO2 would that generate from venting?
Would need to do ~14000/3000 or 4.7 charge cycles like above per day.
[8 empty] | Total Fuel for Vented Power Gen per Day (tons): | 385.9426
[8 empty] | Total Fuel for Vented Power Gen per Year (tons): | 140869.0418
[8 empty] | Total CO2 Emissions (tons): | 249056.466
Lets further assume that we will have 6 GW (net) of flexible CCS generators, and each also fully charges
each day. So lets multiply above value by ~6GW/0.455GW = 13.19.
[8 empty] | Total CO2 Emissions, All Flex CCS Generators (tons): | 3285054.7859
[8 empty] | Total CO2 Emissions, Base Case w/ CO2 Price, From CPP-Affected Units (tons): | 24496830470 | kg
[8 empty] | Total CO2 Emissions, Base Case w/ CO2 Price, From Non-CPP-Affected Units (tons): | 309267797895 | kg
[8 empty] | Total CO2 Emissions, Annual (tons): | 367912419.5892 | ton
[8 empty] | Total CO2 Emissions from 1 Flex CCS Generator as % Of Total Emissions (tons): | 0.8929%

## NumericExample650MW
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  | 4 time steps: | [7 empty] | Same Example Using My Modeling Scheme
|  |  |  | t=0: max generation | [7 empty] | Base CCS Plant
Plant specification: CCS plant type on 'ParameterEstimation650MWPlant', bituminous coal |  |  |  | t=1: store lean solvent (fully charge lean solvent tank) | [7 empty] | 455 | Net Capacity w/ CCS (MW) |  |  |  | **Note that these values ARE not the same as numeric value to left because of different storage amounts.
Plant Parameters w/ CCS |  |  |  | t=2: max generation | [7 empty] | 613.7 | Pre-CCS Net Capacity (MW) |  |  |  | **However, if you scale based on energy to continuous solvent regeneration, results are the same.
Value | Ref to Prior Sheet (for reference) |  |  | t=3: max generation utilizing stored lean solvent | t= | 0 | 1 | 2 | 3 |  |  | 11% | Heat Rate Penalty |  |  |  |  | t= | 0 | 1 | 2 | 3
455 | 455 | MW | Net output |  | Non-flexible CCS | [6 empty] | 25.86% | CCS Capacity Penalty |  |  |  |  | Continuous Gen
158.7 | 158.7 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  | Net Power Output to Grid (MW): | 455 | 455 | 455 | 455 |  |  | 14.86% | Regenerator Capacity Penalty |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 455 | 455 | 455
7431 | 7431 | tons | Lean solvent flow rate |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 7431 | 7431 | 7431 |  |  | 46.53 | Max Energy Input to CO2 Capture System (MWh) | [8 empty] | 1820 | Total Gen
46.53 | 46.53 | MW | CO2 Capture System Use |  | CO2 Capture System Power Use (MW): | 46.53 | 46.53 | 46.53 | 46.53 |  |  | 9.7786 | Net Energy to Grid per Energy Input to CO2 Capture System (MWh/MWh) |  |  |  |  | Use of Stored Solvent, True Pump System
112.17 | . | MW | Regenerator Use |  | Regenerator Power Use (MW): | 112.17 | 112.17 | 112.17 | 112.17 |  |  | 20% | Min loading of steam turbine |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 188.0438
0.021356 | 0.021356 | MWh/ton | Energy required per ton solvent regenerated |  | Total Power Input to Capture CO2 (MW): | 158.7 | 158.7 | 158.7 | 158.7 |  |  | 91 | Min load of steam turbine (MW) |  |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 27.6074 | 0 | 0
0.06123 | 0.06123 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  | Gross Power Output (MW): | 613.7 | 613.7 | 613.7 | 613.7 |  |  | 159.7034 | Tons lean solvent regenerated per unit energy used in CO2 Capture System (tons/MWh) |  |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 18.9226 | 46.53 | 19.2301
0.70681 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator | [5 empty] | 1820 | Total Net Power Delivery to Grid (MW): |  | 0.34833 | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to |  |  |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 19.2301
0.29319 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [5 empty] | 2454.8 | Total Gross Output (MW) |  |  |  | Capture Sys for Stored Lean Solvent (MWh/MWh): |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 9.6166 | 0 | 0
9.7786 | 9.7786 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank | Solvent Storage Generator | [5 empty] | Solvent Regenerated (tons): | 7431 | 7431 | 7431 | 3071.1068
12.1085 | 12.1085 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 455 | 207.3248 | 455 | 271.3101 | [Declines b/c of less continuous solvent regen] | 0 | General Parameters | [5 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 357.2085
[5 empty] | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 242.793 | [Based on discharged amount of stored lean solvent] | 601.3983 | 90% | Heat Rate Penalty Reduction |  |  |  |  | Solvent Flow from Stored Lean Solvent (tons): | 0 | 0 | 0 | 4413.7412
[5 empty] | Total Net Power Output to Grid (MW): | 455 | 207.3248 | 455 | 514.1031 | [Not at max net output because would need full lean solvent tank to get max; see right] | 601.3983 | 95.75% | Capacity Penalty Reduction |  |  | 12.8844 |  | Percent of Continual Solvent Flow Displaced by Stored Solvent (%): | 0 | 0 | 0 | 59.4%
Plant Parameters w/ CCS Using Stored Lean Solvent |  |  |  |  | Total Mass Solvent Continuously Regenerated (tons): | 7431 | 4431 | 7431 | 4431 | [Limited by absorber capacity] | 0 | 3.7895 | Net energy output to grid per energy pumped (MWh/MWh) |  |  |  |  | Total Max Capacity, Accounting for % Continual Regeneration Displaced (MW): | 0 | 0 | 0 | 545.2523
Value | Ref to Prior Sheet (for reference) |  |  |  | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 7431 | 3386 | 7431 | 4431 | [Manually calculated through iterative procedure; set value to that in prior row ('Total Mass Solvent Continuously Regenerated'), then subtract value below in 'Required Adder to Continuous Lean Solvent' row iteratively until that value = 1.] | 0 |  | [Includes energy to regenerator in denominator] |  |  |  |  | Total Solvent Flow Rate (tons): | 7431 | 7431 | 7431 | 7484.848
601.4 | 601.4 | MW | Net output |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 1045 | 0 | 0 | [Discharge entire tank] | 7431 | 12.9389 | Net energy output to grid per energy pumped, excluding energy to regenerator in value this is multiplied with (MWh/MWh) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 27.6074
7431 | 7431 | tons | Lean solvent flow rate |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 3000 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 7431 |  | equals prior parameter*(1+Eregen/Eco2capturesystem) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 329.6011
4.55 | 4.55 | MW | CO2 Capture System Use |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3000 |  | 7431 | 606.9493 | Max total (Base + SS) achievable capcaity (MW) |  |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 545.2523
0 | . | MW | Regenerator Use |  | Mass of Solvent Passed Through Absorber (tons): | 7431 | 4431 | 7431 | 7431 |  | 0 | [10 empty] | 1546.2523 | Total Gen
3000 | . | tons | Lean and rich solvent tank size |  | Mass of Stored Rich Solvent at End of Period (tons): | 3000 | 0 | 0 | 3000 |  | 0 | I model solvent storage generator as additional stand-alone generator, w/ only incremental generation to base CCS facility. | [9 empty] | -0.15041 | Percent Change in Gen w/ Flex CCS vs. Nonflex CCS
3000 | . | tons | Initial mass of stored rich solvent |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 3000 | 3000 | 0 |  | 0 | But solvent storage generator really should replace generation from base CCS facility. | [5 empty] | Use of Stored Solvent, Incremental Pump System
0 | . | tons | Initial mass of stored lean solvent |  | Total Power Input to Continuously Regenerate Solvent (MW): | 158.6964 | 94.6284 | 158.6964 | 94.6284 |  | 0 | When I have full pump load at my stand alone generator, need to inflate this value to scale from incremental pump system | [5 empty] | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 455
0.021356 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 46.529 | 27.7446 | 46.529 | 27.7446 |  | 0 | to true pump system. | [5 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 6.9115 | 0 | 0
0.080931 | 0.080931 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  | Regenerator Power Use, Continuous Regeneration (MW): | 112.1675 | 66.8839 | 112.1675 | 66.8839 |  | 0 | True Pump System | [5 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 18.9226 | 46.53 | 46.53
3.7895 | 3.7895 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 6.5432 | 0 | 0 |  |  | 27.6074 | Max Capacity (MW) |  | [Excludes energy to regenerator] |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 46.53
64.068 | . | MWh | Energy required to fully charge lean solvent storage tank |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 64.068 | 0 | 0 |  | 0 |  | [Steam turbine min load defined as 20%, so must |  |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 9.6166 | 0 | 0
[5 empty] | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 18.7844 | 0 | 0 |  | 0 |  | maintain 20% load through continuous solvent regeneration.] |  |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 89.4269
[5 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 45.2836 | 0 | 0 |  | 0 | 7499.5898 | Tank size to meet max possible output using stored lean solvent (tons) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 6.9115
[5 empty] | CO2 Capture System Power Use, Total (MW): | 46.529 | 46.529 | 46.529 | 27.7446 |  | 0 | 4408.9988 | Solvent pumped at max pump capacity (tons) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 82.5154
[5 empty] | Regenerator Power Use, Total (MW): | 112.1675 | 112.1675 | 112.1675 | 66.8839 |  |  |  |  | [Pump max capacity above does not include energy for regenerator.] |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 544.4269
[5 empty] | Total Power Input to Capture CO2 (MW): | 158.6964 | 158.6964 | 158.6964 | 94.6284 |  |  |  |  | [~80% of tank size can be filled in 1 hour, which makes sense given 20% min load on ST.] | [7 empty] | 1545.4269 | Total Gen
[5 empty] | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 613.6964 | 366.0212 | 613.6964 | 608.7316 |  |  | 58.79% | Percent of solvent necessary for max output that can be stored in 1 hour
[5 empty] | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 7430.9556 | 4431.9752 | 7430.9556 | NA | [8 empty] | IGNORE THIS BOX
[5 empty] | Required Adder to Continuous Lean Solvent (tons): | -0.044431 | 0.97521 | -0.044431 | NA |  |  | Incremental Pump System | [8 empty] | Use of Stored Solvent w/ Backcalculated Regenerator Energy Use
[9 empty] | 1631.4279 | Total Net Power Delivery to Grid (MW) |  | 151.9493 | Max incremental generation w/ stored lean solvent (MW) | [7 empty] | Net Energy Output to Grid (MWh): | 455 | 387.415 | 455 | 455
[9 empty] | -188.5721 | Change in Net Power Delivery to Grid |  | 1877.5166 | Volume of stored lean solvent for max inc. gen (tons) | [7 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 6.9115 | 0 | 0 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[11 empty] | from Cont. Nonflex CCS ops | 40.0962 | Max capacity (MW), based on volume of stored lean solven | [7 empty] | Back-calculated Regenerator Energy Use to Store Lean Solvent (MWh): | 0 | 66.6543 | 0 | 0
[9 empty] | -10.36% | % Change in Net Power Output |  |  |  | necessary for max incremental gen above. | [6 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 39.6185 | 46.53 | 46.53 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[5 empty] | Ratio of E to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.25859 | 0.25853 | 0.25859 | NA |  |  |  |  | [Includes energy to regenerator.] | [6 empty] | Back-calculated Regenerator Energy Use for Continuous Regeneration (MWh): | 112.3402 | 95.6534 | 112.3402 | 112.3402
[5 empty] | Ratio of E to CO2 Capture System to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.075818 | 0.0758 | 0.075818 | NA |  |  | 11.7563 | Max capacity (MW), excluding energy to regenerator. | [7 empty] | Tons Lean Solvent Stored (tons): | 0 | 3444.736 | 0 | 0
[5 empty] | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to Capture Sys for Stored Lean Solvent (MWh/MWh): | NA | 0.34833 | NA | NA |  |  | 6.9115 | Max capacity (MW), excluding energy to regenerator and accounting for limit on how much true pump system can be filled in 1 hour. | [7 empty] | Tons Solvent Continuously Regenerated (tons): | 7439.1386 | 6334.1402 | 7439.1386 | 7439.1386
[12 empty] | 3.9944 | Ratio of pump max capacity in incremental vs. true system | [7 empty] | Tons Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3444.736
[12 empty] | 39.06 | Reduction in base CCS net output per unit energy used to pump lean solvent for storage (MWh/MWh) | [7 empty] | Net Energy to Grid, Tons Continuously Regenerated (MWh): | 455.4985 | 387.8394 | 455.4985 | 455.4985
[5 empty] | Diff in Net Pow Output from Continuous CCS Operations (MW:) | 0 | -247.6752 | 0 | 59.1031 |  |  | 185.0373 | Max capacity of base CCS facility at max pump capacity (MW) | [7 empty] | Net Energy to Grid, Tons Stored Lean Discharged (MWh): | 0 | 0 | 0 | 278.7859 | 278.7805
[5 empty] | Price ($/MWh): | 0 | 10 | 0 | 42 |  |  |  | Check: should be 20% of capacity of base CCS facility | [8 empty] | 613.8702 | 596.2527 | 613.8702 | 613.8702
[5 empty] | Change in Revenues ($): | 0 | -2476.7522 | 0 | 2482.3315 |  |  |  |  | 91 | [6 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 278.7805
[9 empty] | 5.5793 | TOTAL CHANGE IN REVENUES | [10 empty] | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 27.6074
[12 empty] | Extra Generation Unit | [8 empty] | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 251.1731
[9 empty] | Check w/ Alternate Method |  |  | 145.0378 | Max Capacity (MW) | [7 empty] | Total Generation (MWh): | 455 | 380.5035 | 455 | 733.7805
[9 empty] | Power Input to Store Lean Solvent (MW): | 64.068 |  | 20.985 | Ratio of generation at extra generating unit to generation at pumping unit (MW/MW) | [11 empty] | 2024.284 | Total Gen
[9 empty] | Energy Output When Discharge Lean Solvent (MW): | 242.7882
[9 empty] | Net Energy Delivered to Grid Decrease When Storing Lean Solvent (MW): | 247.6752
[9 empty] | Net Energy Delivered to Grid From Continuous Regeneration Decreased When Discharging Stored Lean Solvent (MW): | 183.6899
[9 empty] | Net Power Change (MW): | -188.5768

## NumericExample650MWAbsorber
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. This sheet accounts for no absorber load from solvent regenerated for storage, and calculates difference in | [17 empty] | Same Example Using My Modeling Scheme
net output to grid if assume venting of flue gas when you account for that difference in absorber load. | [17 empty] | Base CCS Plant
Plant specification: CCS plant type on prior sheet, bituminous coal |  |  |  |  | 4 time steps: | [12 empty] | 455 | Net Capacity w/ CCS (MW) |  |  |  | **Note that these values ARE not the same as numeric value to left because of different storage amounts.
Plant Parameters w/ CCS |  |  |  |  | t=0: max generation | [12 empty] | 613.7 | Pre-CCS Net Capacity (MW) |  |  |  | **However, if you scale based on energy to continuous solvent regeneration, results are the same.
Value | Ref to Prior Sheet (for reference) |  |  |  | t=1: store lean solvent (fully charge lean solvent tank) |  |  | t= | 0 | 1 | 2 | 3 | [5 empty] | 11% | Heat Rate Penalty |  |  |  |  | t= | 0 | 1 | 2 | 3
455 | 455 | MW | Net output |  | t=2: max generation |  |  | Non-flexible CCS | [9 empty] | 25.86% | CCS Capacity Penalty |  |  |  |  | Continuous Gen
158.7 | 158.7 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  | t=3: max generation utilizing stored lean solvent |  |  | Net Power Output to Grid (MW): | 455 | 455 | 455 | 455 | [5 empty] | 14.86% | Regenerator Capacity Penalty |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 455 | 455 | 455
7431 | 7431 | tons | Lean solvent flow rate |  |  |  |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 7431 | 7431 | 7431 | [5 empty] | 46.53 | Max Energy Input to CO2 Capture System (MWh) | [8 empty] | 1820 | Total Gen
46.53 | 46.53 | MW | CO2 Capture System Use |  |  |  |  | CO2 Capture System Power Use (MW): | 46.53 | 46.53 | 46.53 | 46.53 | [5 empty] | 9.7786 | Net Energy to Grid per Energy Input to CO2 Capture System (MWh/MWh) |  |  |  |  | Use of Stored Solvent, True Pump System
112.17 | . | MW | Regenerator Use |  |  |  |  | Regenerator Power Use (MW): | 112.17 | 112.17 | 112.17 | 112.17 | [5 empty] | 20% | Min loading of steam turbine |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 95.0541
0.021356 | 0.021356 | MWh/ton | Energy required per ton solvent regenerated |  |  |  |  | Total Power Input to Capture CO2 (MW): | 158.7 | 158.7 | 158.7 | 158.7 | [5 empty] | 91 | Min load of steam turbine (MW) |  |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 37.224 | 0 | 0
0.06123 | 0.06123 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  |  |  | Gross Power Output (MW): | 613.7 | 613.7 | 613.7 | 613.7 | [5 empty] | 159.7034 | Tons lean solvent regenerated per unit energy used in CO2 Capture System (tons/MWh) |  |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 9.306 | 46.53 | 9.7206
0.70681 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator | [8 empty] | 1820 | Total Net Power Delivery to Grid (MW): |  |  |  |  | 0 | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to |  |  |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 9.7206
0.29319 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [8 empty] | 2454.8 | Total Gross Output (MW) | [6 empty] | Capture Sys for Stored Lean Solvent (MWh/MWh): |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 0 | 0 | 0
9.7786 | 9.7786 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank |  |  |  | Solvent Storage Generator | [5 empty] | Solvent Regenerated (tons): | 7431 | 7431 | 7431 | 1552.4107
12.1085 | 12.1085 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  |  |  |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 455 | 207.2407 | 455 | 271.3101 | [Declines b/c of less continuous solvent regen] | 0 |  |  |  | General Parameters | [5 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 481.6361
0.33143 | 0.33143 | tons fuel/MWh | Gross Heat Rate |  |  |  |  | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 242.793 | [Based on discharged amount of stored lean solvent] | 601.3983 |  |  |  | 90% | Heat Rate Penalty Reduction |  |  |  |  | Solvent Flow from Stored Lean Solvent (tons): | 0 | 0 | 0 | 5951.1944
[8 empty] | Total Net Power Output to Grid (MW): | 455 | 207.2407 | 455 | 514.1031 | [Not at max net output because would need full lean solvent tank to get max; see right] | 601.3983 |  |  |  | 95.75% | Capacity Penalty Reduction |  |  | 12.8844 |  | Percent of Continual Solvent Flow Displaced by Stored Solvent (%): | 0 | 0 | 0 | 80.09%
Plant Parameters w/ CCS While Discharging Stored Lean Solvent | [7 empty] | Total Mass Solvent Continuously Regenerated (tons): | 7431 | 4431 | 7431 | 4431 | [Limited by absorber capacity] | 0 |  |  |  | 3.7895 | Net energy output to grid per energy pumped (MWh/MWh) |  |  |  |  | Total Max Capacity, Accounting for % Continual Regeneration Displaced (MW): | 0 | 0 | 0 | 576.6902
Value | Ref to Prior Sheet (for reference) | [6 empty] | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 7431 | 3384.6264 | 7431 | 4431 | [Manually calculated through iterative procedure; set value to that in prior row ('Total Mass Solvent Continuously Regenerated'), then subtract value below in 'Required Adder to Continuous Lean Solvent' row iteratively until that value = 1.] | 0 |  |  |  |  | [Includes energy to regenerator in denominator] |  |  |  |  | Total Solvent Flow Rate (tons): | 7431 | 7431 | 7431 | 7503.6051
601.4 | 601.4 | MW | Net output |  |  |  |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 1046.3736 | 0 | 0 | [Discharge entire tank] | 7431 |  |  |  | 12.9389 | Net energy output to grid per energy pumped, excluding energy to regenerator in value this is multiplied with (MWh/MWh) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 37.224
7431 | 7431 | tons | Lean solvent flow rate |  |  |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 3000 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 7431 |  |  |  |  | equals prior parameter*(1+Eregen/Eco2capturesystem) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 444.4121
4.55 | 4.55 | MW | CO2 Capture System Use |  |  |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3000 |  | 7431 |  |  |  | 606.9493 | Max total (Base + SS) achievable capcaity (MW) |  |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 576.6902
0 | . | MW | Regenerator Use |  |  |  |  | Mass of Solvent Passed Through Absorber (tons): | 7431 | 4431 | 7431 | 7431 |  | 0 | [13 empty] | 1577.6902 | Total Gen
3000 | . | tons | Lean and rich solvent tank size |  |  |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 3000 | 0 | 0 | 3000 |  | 0 |  |  |  | I model solvent storage generator as additional stand-alone generator, w/ only incremental generation to base CCS facility. | [9 empty] | -0.13314 | Percent Change in Gen w/ Flex CCS vs. Nonflex CCS
3000 | . | tons | Initial mass of stored rich solvent |  |  |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 3000 | 3000 | 0 |  | 0 |  |  |  | But solvent storage generator really should replace generation from base CCS facility. | [5 empty] | Use of Stored Solvent, Incremental Pump System
0 | . | tons | Initial mass of stored lean solvent |  |  |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 158.6964 | 94.6284 | 158.6964 | 94.6284 |  | 0 |  |  |  | When I have full pump load at my stand alone generator, need to inflate this value to scale from incremental pump system | [5 empty] | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 455
0.021356 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 46.529 | 27.7446 | 46.529 | 27.7446 |  | 0 |  |  |  | to true pump system. | [5 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 9.319 | 0 | 0
0.080931 | 0.080931 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 112.1675 | 66.8839 | 112.1675 | 66.8839 |  | 0 |  |  |  | True Pump System | [5 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 9.306 | 46.53 | 46.53
3.7895 | 3.7895 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  |  |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 6.5518 | 0 | 0 | [5 empty] | 37.224 | Max Capacity (MW) |  | [Excludes energy to regenerator] |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 46.53
64.068 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 64.068 | 0 | 0 |  | 0 |  |  |  |  | [Steam turbine min load defined as 20%, so must |  |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 0 | 0 | 0
0.33821 | 0.33821 | tons/MWh | Net heat rate |  |  |  |  | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 15.5175 | 0 | 0 | [adjust downward to account for fact that 17% of power is used in absorber, and that power is not used when continuously regenerating solvent] | 0 |  |  |  |  | maintain 20% load through continuous solvent regeneration.] |  |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 120.5772
[8 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 45.2836 | 0 | 0 |  | 0 |  |  |  | 7499.5898 | Tank size to meet max possible output using stored lean solvent (tons) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 9.319
Plant Parameters w/ CCS While Charging Stored Lean Solvent | [7 empty] | CO2 Capture System Power Use, Total (MW): | 46.529 | 43.2621 | 46.529 | 27.7446 |  | 0 |  |  |  | 5944.8 | Solvent pumped at max pump capacity (tons) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 111.2582
Value | Ref to Prior Sheet (for reference) | [6 empty] | Regenerator Power Use, Total (MW): | 112.1675 | 112.1675 | 112.1675 | 66.8839 | [7 empty] | [Pump max capacity above does not include energy for regenerator.] |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 575.5772
0.34879 | 0.34879 | MWh/MWh | MWh for extra solvent / MWh for solvent to be regenerated |  |  |  |  | Total Power Input to Capture CO2 (MW): | 158.6964 | 155.4296 | 158.6964 | 94.6284 | [7 empty] | [~80% of tank size can be filled in 1 hour, which makes sense given 20% min load on ST.] | [7 empty] | 1576.5772 | Total Gen
0.34879 | 0.34879 | ton solvent/ton solvent | ton extra solvent necessary / ton solvent to be stored regenerated |  |  |  |  | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 613.6964 | 362.6703 | 613.6964 | 608.7316 | [5 empty] | 79.27% | Percent of solvent necessary for max output that can be stored in 1 hour
0.0070782 | 0.0070782 | ton fuel/ton solvent | tons fuel / ton solvent regenerated (continuously or for storage) |  |  |  |  | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 7430.9556 | 4391.4001 | 7430.9556 | NA
|  |  |  | This value assumes full operation of absorber! |  |  |  | Fuel for Net Power Output (tons): | 150.8017 | 68.6863 | 150.8017 | 89.9209 | [5 empty] | Incremental Pump System | [8 empty] | Use of Stored Solvent w/ Backcalculated Regenerator Energy Use
[8 empty] | Fuel for Continuous Solvent Regen (tons): | 52.5983 | 31.3636 | 52.5983 | 31.3636 |  | 52.5971 | 51.5144 | 52.5971 | 31.3629 | 151.9493 | Max incremental generation w/ stored lean solvent (MW) | [7 empty] | Net Energy Output to Grid (MWh): | 455 | 363.8729 | 455 | 455
[8 empty] | Fuel for Stored Solvent Regen (tons): | 0 | 21.2347 | 0 | 0 | [5 empty] | 1877.5166 | Volume of stored lean solvent for max inc. gen (tons) | [7 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 9.319 | 0 | 0 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[8 empty] | Fuel for Discharged Stored Lean Solvent (tons): | 0 | 0 | 0 | 82.1152 | [5 empty] | 40.0962 | Max capacity (MW), based on volume of stored lean solven | [7 empty] | Back-calculated Regenerator Energy Use to Store Lean Solvent (MWh): | 0 | 89.8722 | 0 | 0
[8 empty] | Total Fuel (tons): | 203.4 | 121.2846 | 203.4 | 203.3998 | [7 empty] | necessary for max incremental gen above. | [6 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 37.211 | 46.53 | 46.53 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[8 empty] | Fuel Use Accounting for No Power Use in Absorber for Stored Lean Solvent | [11 empty] | [Includes energy to regenerator.] | [6 empty] | Back-calculated Regenerator Energy Use for Continuous Regeneration (MWh): | 112.3402 | 89.8408 | 112.3402 | 112.3402
[8 empty] | Fuel for Total Solvent Regen (tons): | 52.5971 | 51.5144 | 52.5971 | 31.3629 | [5 empty] | 11.7563 | Max capacity (MW), excluding energy to regenerator. | [7 empty] | Tons Lean Solvent Stored (tons): | 0 | 4644.6523 | 0 | 0
[8 empty] | Fuel for Net Power Output (tons): | 150.8017 | 68.6863 | 150.8017 | 89.9209 | [5 empty] | 9.319 | Max capacity (MW), excluding energy to regenerator and accounting for limit on how much true pump system can be filled in 1 hour. | [7 empty] | Tons Solvent Continuously Regenerated (tons): | 7439.1386 | 5949.2324 | 7439.1386 | 7439.1386
[8 empty] | Total Fuel (tons): | 203.3988 | 120.2006 | 203.3988 | 203.3991 | [5 empty] | 3.9944 | Ratio of pump max capacity in incremental vs. true system | [7 empty] | Tons Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 4644.6523
[8 empty] | Difference in Fuel Between Two Approaches (tons): | -0.0011812 | -1.0839 | -0.0011812 | -0.00070435 | [5 empty] | 39.06 | Reduction in base CCS net output per unit energy used to pump lean solvent for storage (MWh/MWh) | [7 empty] | Net Energy to Grid, Tons Continuously Regenerated (MWh): | 455.4985 | 364.2715 | 455.4985 | 455.4985
[18 empty] | 91.0003 | Max capacity of base CCS facility at max pump capacity (MW) | [7 empty] | Net Energy to Grid, Tons Stored Lean Discharged (MWh): | 0 | 0 | 0 | 375.8964 | 375.889
[12 empty] | 1631.3438 | Total Net Power Delivery to Grid (MW) | [5 empty] | Check: should be 20% of capacity of base CCS facility | [8 empty] | 613.8702 | 590.1159 | 613.8702 | 613.8702
[6 empty] | Percent of Energy Use in CO2 Capture Excluding Regenerator by Absorber (%): | 17.39% | Fuel for Vented Power Gen (tons): |  | 83.1982 |  | -188.6562 | Change in Net Power Delivery to Grid from Cont. Nonflex CCS ops | [6 empty] | 91 | [6 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 375.889
[8 empty] | Net Electricity from Extra Fuel (MWh): |  | 251.0262 |  | -10.37% | % Change in Net Power Output | [13 empty] | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 37.224
[8 empty] | Total Net Electricity (MWh): |  | 458.2669 | [7 empty] | Extra Generation Unit | [8 empty] | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 338.665
[8 empty] | Difference in Net Electricity Generation when Account for Lower Absorber Load (MWh): |  | 3.2669 | 0.718% | [6 empty] | 142.6303 | Max Capacity (MW) | [7 empty] | Total Generation (MWh): | 455 | 354.5539 | 455 | 830.889
[18 empty] | 15.3053 | Ratio of generation at extra generating unit to generation at pumping unit (MW/MW) | [11 empty] | 2095.4429 | Total Gen

## ExAsModeledInPLEXOS
This sheet provides example calculations of flexible CCS using only the parameters and relationships that I use in PLEXOS.
Check this against 'NumericExample650MW' to see if roughly the same. (Whether check against left or right side set of calculations depends on Pump Load value chosen; see note to right of time series data.)
4 time steps:
CONSTRAINTS |  |  |  | t=0: max generation
p_extra = (A-1)*p_pump |  |  |  | t=1: store lean solvent (fully charge lean solvent tank)
t=2: max generation
p_base = P_base - B*E*(1+D)*m_pump |  |  |  | t=3: max generation utilizing stored lean solvent
(1+D)*E*m_pump + HRP*p_base = HRP*P_base
|  |  |  | t= | 0 | 1 | 2 | 3
ELECTRICITY GENERATION
PLANT PARAMETERS |  |  |  | Base CCS Output (MW): | 455.1 | 207.6231 | 455.1 | 455.1 |  | *Use 4.7 MW for pump load to mimic left set of calculations in sheet 'NumericExample650MW'
615 | Pre-CCS Net Output (MW) |  |  | Pump Generation (MW): | 0 | 0 | 0 | 4.7 |  | *Use max pump load (~6.966 MW) to mimic right set of calculations in sheet 'NumericExample650MW'
8.7 | Pre-CCS Net Heat Rate (MMBtu/MWh) |  |  | Generation from Extra Generator (MW): | 0 | 0 | 0 | 56.118
33% | CCS Heat Rate Penalty |  |  | Total Discharge with Stored Lean (MW): | 0 | 0 | 0 | 60.818 |  |  |  |  | Sources of Fuel Use
26% | CCS Capacity Penalty |  |  | Pump Load (MW): | 0 | 4.7 | 0 | 0 | [Not inc. regenerator E input.] |  |  |  | Net power to grid
11.571 | Post-CCS Net Heat Rate (MMBtu/MWh) |  |  | Generation at Pump Dummy (MW): | 0 | 4.7 | 0 | 0 | [5 empty] | Net power to grid from base CCS facility
8.7 | Post-CCS Gross Heat Rate (MMBtu/MWh) |  |  | Generation for Solvent to Bind CO2 for Fuel for Stored Lean Solvent (MW): | 0 | 6.5326 | 0 | 0 | [5 empty] | Net power to grid from discharged stored lean solvent
455.1 | Post-CCS Net Output (MW) |  |  | Actual Pump Load (MW): | 0 | 18.7718 | 0 | 0 |  |  |  |  | Power to CO2 capture system for solvent for net power to grid
|  |  |  | Actual Generation for Solvent to Bind CO2 for Fuel for Stored Lean Solvent (MW): | 0 | 6.5326 | 0 | 0 | [5 empty] | [This is captured w/ net power to grid by using net heat rate at base facility]
FLEX CCS CONSTANTS |  |  |  | FUEL USE | [8 empty] | Stored lean solvent
A= | 12.94 |  |  | Fuel Use, Base CCS Plant using Net Heat Rate (MMBtu): | 5265.9621 | 2402.4069 | 5265.9621 | 5265.9621 |  |  |  |  | Solvent to capture CO2 from fuel for stored lean solvent
B= | 9.78 |  |  | Fuel Use, Base CCS Plant using Gross Heat Rate (MMBtu): | 3959.37 | 1806.321 | 3959.37 | 3959.37 | [5 empty] | [Prior two fuel sources are both captured in Fuel Use, Storing Lean Solvent]
D= | 0.348 |  |  | Fuel Use, Gen w/ Stored Lean (MMBtu): | 0 | 0 | 0 | 546.5774
E = | 3.994 |  |  | Fuel Use, Storing Lean Solvent (i.e., from Pump Dummy) (MMBtu): | 0 | 751.2606 | 0 | 0 | [scale up to "true" pump load, then calculate fuel use]
|  |  |  | Fuel Use, Gen for Solv to Bind CO2 for Fuel for Stored Lean Solvent (MMBtu): | 0 | 56.8335 | 0 | 0 | [accounted for already in above row through (1+D) term]
FLEX CCS PARAMETERS |  |  |  | Total Fuel Use, Gross Heat Rate (MMBtu): | 3959.37 | 2614.4151 | 3959.37 | 4505.9474 | [needs to have separate term for fuel use in co2 capture sytsem of continuous generation]
6.3508 | Pump Load (MW) |  |  | Total Fuel Use, Net Heat Rate (MMBtu): | 5265.9621 | 3153.6675 | 5265.9621 | 5812.5395
90% | Heat Rate Penalty Reduction (%) |  |  | Fuel Use, Net Heat Rate, Base CCS (tons): | 201.2982 | 91.8351 | 201.2982 | 201.2982
87.31% | Capacity Penalty Reduction (%) |  |  | Fuel Use, Gen w/ Stored Lean (tons): | 0 | 0 | 0 | 20.8936 | 222.1919
58.79% | % of Stored Lean Solvent Discharged at Max Output that Can Be Stored in 1 Hour |  |  | Fuel Use, Storing Lean Solvent (tons): | 0 | 28.7179 | 0 | 0
594.705 | Net Output with Stored Lean Solvent (MW) |  |  | Total Fuel Use, Gross Heat Rate (tons): | 151.3521 | 99.9394 | 151.3521 | 172.2457
139.605 | Incremental Gen with Stored Lean Solvent (MW) |  |  | Total Fuel Use, Net Heat Rate (tons): | 201.2982 | 120.553 | 201.2982 | 222.1919
0.0809 | Net E to Grid / Ton Stored Lean Solvent Discharged (MWh/tons) |  |  | Total Net Output (MW): | 455.1 | 207.6231 | 455.1 | 515.918
0.00626 | E to CO2 Capture System Exc. Regenerator / Tons Lean Solvent Discharged in Normal CCS Operations (MWh/tons) |  |  |  |  | 0.59888
8.9871 | Flex CCS Net Heat Rate When Discharging Stored Lean Solvent (MMBtu/MWh)
2.4125 | E to Regenerator / E to CO2 Capture System (MWh/MWh) |  |  | FROM OTHER SHEET
|  |  |  | Fuel for Net Power Output Toal (tons): | 203.4 | 100.0499 | 203.4 | 121.2846 |  |  | Net power output very similar on regular hours
FUEL HEAT CONTENT |  |  |  | Fuel for Discharged Stored Lean Solvent (tons): | 0 | 0 | 0 | 82.1152 | 203.3998 |  | Joint fuel consumption of base CCS + discharged lean similar
From IECM |  |  |  | Fuel for Stored Solvent Regen (tons): | 0 | 21.2347 | 0 | 0 |  |  | Stored solvent regen higher than it should be
Heating Value = Total Plant Input (MMBtu/hr) / Fuel Flow Rate (tons/hr) |  |  |  | Total Fuel (tons): | 203.4 | 121.2846 | 203.4 | 203.3998 |  |  |  | But share of fuel consumption when charging roughly equal in both calculations
Assume Appalachian Low Sulfur (bituminous) | [5 empty] | 0.59629 |  |  |  |  | During discharge, fuel output too high (b/c fuel use at base CCS facility too high)
13080 | Heating Value (Btu/lb)
26.16 | Heating Value (MMBtu/ton)
|  | 0.33 | IECM Gross HR (ton/MWh)
|  | 8.6328 | Gross HR (ton/MWh)

## ExAsModeledInPLEXOSVent
This sheet provides example calculations of flexible CCS using only the parameters and relationships that I use in PLEXOS.
This sheet assumes venting is done when charging stored lean solvent, such that fuel input remains the same. In this sheet, that generation from vented CO2 comes from base CCS facility, which has a higher net heat rate than it should when venting, so fuel use is larger than in other sheet.
4 time steps:
CONSTRAINTS |  |  |  | t=0: max generation
p_extra = (A-1)*p_pump |  |  |  | t=1: store lean solvent (fully charge lean solvent tank)
t=2: max generation
p_base = P_base - B*E*(1+D)*m_pump |  |  |  | t=3: max generation utilizing stored lean solvent
(1+D)*E*m_pump + HRP*p_base = HRP*P_base
|  |  |  | t= | 0 | 1 | 2 | 3
ELECTRICITY GENERATION
PLANT PARAMETERS |  |  |  | Base CCS Output (MW): | 455.1 | 455.1 | 455.1 | 455.1 |  | *Use 4.7 MW for pump load to mimic left set of calculations in sheet 'NumericExample650MW'
615 | Pre-CCS Net Output (MW) |  |  | Pump Generation (MW): | 0 | 0 | 0 | 4.7 |  | *Use max pump load (~6.966 MW) to mimic right set of calculations in sheet 'NumericExample650MW'
8.7 | Pre-CCS Net Heat Rate (MMBtu/MWh) |  |  | Generation from Extra Generator (MW): | 0 | 0 | 0 | 56.118
33% | CCS Heat Rate Penalty |  |  | Total Discharge with Stored Lean (MW): | 0 | 0 | 0 | 60.818 |  |  |  |  | Sources of Fuel Use
26% | CCS Capacity Penalty |  |  | Pump Load (MW): | 0 | 4.7 | 0 | 0 | [Not inc. regenerator E input.] |  |  |  | Net power to grid
11.571 | Post-CCS Net Heat Rate (MMBtu/MWh) |  |  | Generation at Pump Dummy (MW): | 0 | 4.7 | 0 | 0 | [5 empty] | Net power to grid from base CCS facility
8.7 | Post-CCS Gross Heat Rate (MMBtu/MWh) |  |  | Generation from Vented CO2 While Charging (MW): | [9 empty] | Net power to grid from discharged stored lean solvent
455.1 | Post-CCS Net Output (MW) |  |  | Generation for Solvent to Bind CO2 for Fuel for Stored Lean Solvent (MW): | 0 | 6.5326 | 0 | 0 |  |  |  |  | Power to CO2 capture system for solvent for net power to grid
[This is captured w/ net power to grid by using net heat rate at base facility]
FLEX CCS CONSTANTS |  |  |  | FUEL USE | [8 empty] | Stored lean solvent
A= | 12.94 |  |  | Fuel Use, Base CCS Plant using Net Heat Rate (MMBtu): | 5265.9621 | 5265.9621 | 5265.9621 | 5265.9621 |  |  |  |  | Solvent to capture CO2 from fuel for stored lean solvent
B= | 9.78 |  |  | Fuel Use, Base CCS Plant using Gross Heat Rate (MMBtu): | 3959.37 | 3959.37 | 3959.37 | 3959.37 | [5 empty] | [Prior two fuel sources are both captured in Fuel Use, Storing Lean Solvent]
D= | 0.348 |  |  | Fuel Use, Gen w/ Stored Lean (MMBtu): | 0 | 0 | 0 | 546.5774
E = | 3.994 |  |  | Fuel Use, Storing Lean Solvent (i.e., from Pump Dummy) (MMBtu): | 0 | 751.2606 | 0 | 0 | [scale up to "true" pump load, then calculate fuel use]
|  |  |  | Fuel Use, Gen for Solv to Bind CO2 for Fuel for Stored Lean Solvent (MMBtu): | 0 | 56.8335 | 0 | 0 | [accounted for already in above row through (1+D) term]
FLEX CCS PARAMETERS |  |  |  | Total Fuel Use, Gross Heat Rate (MMBtu): | 3959.37 | 4767.4641 | 3959.37 | 4505.9474 | [needs to have separate term for fuel use in co2 capture sytsem of continuous generation]
6.3508 | Pump Load (MW) |  |  | Total Fuel Use, Net Heat Rate (MMBtu): | 5265.9621 | 6017.2227 | 5265.9621 | 5812.5395
90% | Heat Rate Penalty Reduction (%) |  |  | Fuel Use, Net Heat Rate, Base CCS (tons): | 201.2982 | 201.2982 | 201.2982 | 201.2982
87.31% | Capacity Penalty Reduction (%) |  |  | Fuel Use, Gen w/ Stored Lean (tons): | 0 | 0 | 0 | 20.8936 | 222.1919
58.79% | % of Stored Lean Solvent Discharged at Max Output that Can Be Stored in 1 Hour |  |  | Fuel Use, Storing Lean Solvent (tons): | 0 | 28.7179 | 0 | 0
594.705 | Net Output with Stored Lean Solvent (MW) |  |  | Total Fuel Use, Gross Heat Rate (tons): | 151.3521 | 182.2425 | 151.3521 | 172.2457
139.605 | Incremental Gen with Stored Lean Solvent (MW) |  |  | Total Fuel Use, Net Heat Rate (tons): | 201.2982 | 230.0162 | 201.2982 | 222.1919
0.0809 | Net E to Grid / Ton Stored Lean Solvent Discharged (MWh/tons) |  |  | Total Net Output (MW): | 455.1 | 455.1 | 455.1 | 515.918
0.00626 | E to CO2 Capture System Exc. Regenerator / Tons Lean Solvent Discharged in Normal CCS Operations (MWh/tons) |  |  |  |  | 1.1427
8.9871 | Flex CCS Net Heat Rate When Discharging Stored Lean Solvent (MMBtu/MWh)
2.4125 | E to Regenerator / E to CO2 Capture System (MWh/MWh) |  |  | FROM OTHER SHEET
|  |  |  | Fuel for Net Power Output Toal (tons): | 203.4 | 100.0499 | 203.4 | 121.2846 |  |  | Net power output very similar on regular hours
FUEL HEAT CONTENT |  |  |  | Fuel for Discharged Stored Lean Solvent (tons): | 0 | 0 | 0 | 82.1152 | 203.3998 |  | Joint fuel consumption of base CCS + discharged lean similar
From IECM |  |  |  | Fuel for Stored Solvent Regen (tons): | 0 | 21.2347 | 0 | 0 |  |  | Stored solvent regen higher than it should be
Heating Value = Total Plant Input (MMBtu/hr) / Fuel Flow Rate (tons/hr) |  |  |  | Total Fuel (tons): | 203.4 | 121.2846 | 203.4 | 203.3998 |  |  |  | But share of fuel consumption when charging roughly equal in both calculations
Assume Appalachian Low Sulfur (bituminous) | [5 empty] | 0.59629 |  |  |  |  | During discharge, fuel output too high (b/c fuel use at base CCS facility too high)
13080 | Heating Value (Btu/lb)
26.16 | Heating Value (MMBtu/ton)
|  | 0.33 | IECM Gross HR (ton/MWh)
|  | 8.6328 | Gross HR (ton/MWh)

## ExAsModeledInPLEXOSVent@VentGen
This sheet provides example calculations of flexible CCS using only the parameters and relationships that I use in PLEXOS.
This sheet assumes venting is done when charging stored lean solvent, such that fuel input remains the same. In this sheet, that generation from vented CO2 is done at venting generator, so fuel use is closer to what it should be.
4 time steps:
CONSTRAINTS |  | t=0: max generation
p_extra = (A-1)*p_pump |  | t=1: store lean solvent (fully charge lean solvent tank)
t=2: max generation
p_base = P_base - B*E*(1+D)*m_pump |  | t=3: max generation utilizing stored lean solvent
(1+D)*E*m_pump + HRP*p_base = HRP*P_base
|  | t= | 0 | 1 | 2 | 3
ELECTRICITY GENERATION
PLANT PARAMETERS |  | Base CCS Output (MW): | 455.1 | 120.7429 | 455.1 | 455.1 |  | *Use 4.7 MW for pump load to mimic left set of calculations in sheet 'NumericExample650MW'
615 | Pre-CCS Net Output (MW) | Pump Generation (MW): | 0 | 0 | 0 | 6.35 |  | *Use max pump load (~6.966 MW) to mimic right set of calculations in sheet 'NumericExample650MW'
8.7 | Pre-CCS Net Heat Rate (MMBtu/MWh) | Generation from Extra Generator (MW): | 0 | 0 | 0 | 75.819
33% | CCS Heat Rate Penalty | Total Discharge with Stored Lean (MW): | 0 | 0 | 0 | 82.169 |  |  | Sources of Fuel Use
26% | CCS Capacity Penalty | Pump Load (MW): | 0 | 6.35 | 0 | 0 | [Not inc. regenerator E input.] |  | Net power to grid
11.571 | Post-CCS Net Heat Rate (MMBtu/MWh) | Generation at Pump Dummy (MW): | 0 | 6.35 | 0 | 0 |  |  |  | Net power to grid from base CCS facility
8.7 | Post-CCS Gross Heat Rate (MMBtu/MWh) | Generation from Vented CO2 While Charging (MW): | 0 | 334.3571 | 0 | 0 |  |  |  | Net power to grid from discharged stored lean solvent
455.1 | Post-CCS Net Output (MW) | Generation for Solvent to Bind CO2 for Fuel for Stored Lean Solvent (MW): | 0 | 8.8259 | 0 | 0 |  |  | Power to CO2 capture system for solvent for net power to grid
[This is captured w/ net power to grid by using net heat rate at base facility]
FLEX CCS CONSTANTS |  | FUEL USE | [6 empty] | Stored lean solvent
A= | 12.94 | Fuel Use, Base CCS Plant using Net Heat Rate (MMBtu): | 5265.9621 | 1397.1162 | 5265.9621 | 5265.9621 |  |  | Solvent to capture CO2 from fuel for stored lean solvent
B= | 9.78 | Fuel Use, Gen w/ Stored Lean (MMBtu): | 0 | 0 | 0 | 738.461 |  |  |  | [Prior two fuel sources are both captured in Fuel Use, Storing Lean Solvent]
D= | 0.348 | Fuel Use, Venting Gen (MMBtu): | 0 | 3004.9006 | 0 | 0
E = | 3.994 | Fuel Use, Storing Lean Solvent (i.e., from Pump Dummy) (MMBtu): | 0 | 1015.0011 | 0 | 0 | [scale up to "true" pump load, then calculate fuel use]
|  | Total Fuel Use, Net Heat Rate (MMBtu): | 5265.9621 | 2412.1173 | 5265.9621 | 6004.4231 | [accounted for already in above row through (1+D) term]
FLEX CCS PARAMETERS |  | Fuel Use, Net Heat Rate, Base CCS (tons): | 201.2982 | 53.4066 | 201.2982 | 201.2982 | [needs to have separate term for fuel use in co2 capture sytsem of continuous generation]
6.3508 | Pump Load (MW) | Fuel Use, Gen w/ Stored Lean (tons): | 0 | 0 | 0 | 28.2286
90% | Heat Rate Penalty Reduction (%) | Fuel Use, Venting Gen (tons): | 0 | 114.8662 | 0 | 0
87.31% | Capacity Penalty Reduction (%) | Fuel Use, Total Net Power to Grid (tons): | 201.2982 | 168.2728 | 201.2982 | 229.5269
58.79% | % of Stored Lean Solvent Discharged at Max Output that Can Be Stored in 1 Hour | Fuel Use, Storing Lean Solvent (tons): | 0 | 38.7997 | 0 | 0
594.705 | Net Output with Stored Lean Solvent (MW) | Total Fuel Use (tons): | 201.2982 | 207.0725 | 201.2982 | 229.5269
139.605 | Incremental Gen with Stored Lean Solvent (MW) | Total Net Output (MW): | 455.1 | 455.1 | 455.1 | 537.269
0.0809 | Net E to Grid / Ton Stored Lean Solvent Discharged (MWh/tons) | Operational Cost, Base CCS Gen ($): | 603.8947 | 160.2198 | 603.8947 | 603.8947
0.00626 | E to CO2 Capture System Exc. Regenerator / Tons Lean Solvent Discharged in Normal CCS Operations (MWh/tons) | Operational Cost, Vent Gen ($): | 0 | 344.5987 | 0 | 0
8.9871 | Flex CCS Net Heat Rate When Discharging Stored Lean Solvent (MMBtu/MWh) | Operational Cost, Pump Gen ($): | 0 | 116.3992 | 0 | 0
2.4125 | E to Regenerator / E to CO2 Capture System (MWh/MWh) | Operational Cost, Extra Gen when Discharging ($): | 0 | 0 | 0 | 0
|  | Total Operational Cost ($): | 603.8947 | 621.2176 | 603.8947 | 603.8947
FUEL HEAT CONTENT
From IECM
Heating Value = Total Plant Input (MMBtu/hr) / Fuel Flow Rate (tons/hr)
Assume Appalachian Low Sulfur (bituminous)
13080 | Heating Value (Btu/lb)
26.16 | Heating Value (MMBtu/ton)
FUEL PRICE
3 | Fuel price for base CCS and pump facility and venting gen($/ton)
0 | Fuel price for extra generator during discharge ($/ton)
PLANT VOM
1 | Variable O&M cost for all plants ($/MWh)

## NumericExampleDiffTankSize
Reran calculations on NumericExampleV2 sheet with a different tank size to check whether the ratio in cell V45 (E to capture CO2 from fuel used to store lean solvent to E used to store lean solvent) is the same.
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  |  | 4 time steps:
t=0: max generation
Plant specification: CCS plant type on prior sheet, bituminous coal | [5 empty] | t=1: store lean solvent (fully charge lean solvent tank)
Plant Parameters w/ CCS | [5 empty] | t=2: max generation
Value | Ref to Prior Sheet (for reference) |  |  |  |  | t=3: max generation utilizing stored lean solvent
455 | 455 | MW | Net output
158.7 | 158.7 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  |  |  | t= | 0 | 1 | 2 | 3
7431 | 7431 | tons | Lean solvent flow rate |  |  |  | Non-flexible CCS
46.53 | 46.53 | MW | CO2 Capture System Use |  |  |  | Net Power Output to Grid (MW): | 455 | 455 | 455 | 455
112.17 | . | MW | Regenerator Use |  |  |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 7431 | 7431 | 7431
0.021356 | 0.021356 | MWh/ton | Energy required per ton solvent regenerated |  |  |  | CO2 Capture System Power Use (MW): | 46.53 | 46.53 | 46.53 | 46.53
0.06123 | 0.06123 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  |  | Regenerator Power Use (MW): | 112.17 | 112.17 | 112.17 | 112.17
0.70681 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator |  |  |  | Total Power Input to Capture CO2 (MW): | 158.7 | 158.7 | 158.7 | 158.7
0.29319 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [7 empty] | 1820 | Total Net Power Delivery to Grid (MW):
9.7786 | 9.7786 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank
12.1085 | 12.1085 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  |  |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 455 | 289.9241 | 455 | 332.5401 | [Declines b/c of less continuous solvent regen] | 0
[7 empty] | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 161.862 | [Based on discharged amount of stored lean solvent] | 601.3983
[7 empty] | Total Net Power Output to Grid (MW): | 455 | 289.9241 | 455 | 494.4021 | [Not at max net output because would need full lean solvent tank to get max; see right] | 601.3983
Plant Parameters w/ CCS Using Stored Lean Solvent | [6 empty] | Total Mass Solvent Continuously Regenerated (tons): | 7431 | 5431 | 7431 | 5431 | [Limited by absorber capacity] | 0
Value | Ref to Prior Sheet (for reference) | [5 empty] | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 7431 | 4735 | 7431 | 5431 |  | 0
601.4 | 601.4 | MW | Net output |  |  |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 696 | 0 | 0 | [Discharge entire tank] | 7431
7431 | 7431 | tons | Lean solvent flow rate |  |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 2000 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 7431
4.55 | 4.55 | MW | CO2 Capture System Use |  |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 2000 |  | 7431
0 | . | MW | Regenerator Use |  |  |  | Mass of Solvent Passed Through Absorber (tons): | 7431 | 5431 | 7431 | 7431 |  | 0
2000 | . | tons | Lean and rich solvent tank size |  |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 2000 | 0 | 0 | 2000 |  | 0
2000 | . | tons | Initial mass of stored rich solvent |  |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 2000 | 2000 | 0 |  | 0
0 | . | tons | Initial mass of stored lean solvent |  |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 158.6964 | 115.9844 | 158.6964 | 115.9844 |  | 0
0.021356 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 46.529 | 34.006 | 46.529 | 34.006 |  | 0
0.080931 | 0.080931 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 112.1675 | 81.9784 | 112.1675 | 81.9784 |  | 0
3.7895 | 3.7895 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 4.358 | 0 | 0
42.712 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 42.712 | 0 | 0 |  | 0
[7 empty] | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 12.5229 | 0 | 0 |  | 0
[7 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 30.1891 | 0 | 0 |  | 0
[7 empty] | CO2 Capture System Power Use, Total (MW): | 46.529 | 46.529 | 46.529 | 34.006 |  | 0
[7 empty] | Regenerator Power Use, Total (MW): | 112.1675 | 112.1675 | 112.1675 | 81.9784
[7 empty] | Total Power Input to Capture CO2 (MW): | 158.6964 | 158.6964 | 158.6964 | 115.9844
|  |  |  | 3386 |  |  | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 613.6964 | 448.6205 | 613.6964 | 610.3866
[7 empty] | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 7430.9556 | 5432.1301 | 7430.9556 | NA
[7 empty] | Required Adder to Continuous Lean Solvent (tons): | -0.044431 | 1.1301 | -0.044431 | NA
[11 empty] | 1694.3262 | Total Net Power Delivery to Grid (MW)
[11 empty] | -125.6738 | Change in Net Power Delivery to Grid from Cont. Nonflex CCS ops
[11 empty] | -6.905% | % Change in Net Power Output
[7 empty] | Ratio of E to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.25859 | 0.25854 | 0.25859 | NA
[7 empty] | Ratio of E to CO2 Capture System to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.075818 | 0.075801 | 0.075818 | NA
[7 empty] | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to Capture Sys for Stored Lean Solvent (MWh/MWh): | NA | 0.348 | NA | NA
[7 empty] | Diff in Net Pow Output from Continuous CCS Operations (MW:) | 0 | -165.0759 | 0 | 39.4021
[7 empty] | Price ($/MWh): | 0 | 10 | 0 | 42
[7 empty] | Change in Revenues ($): | 0 | -1650.7595 | 0 | 1654.8895
[11 empty] | 4.13 | TOTAL CHANGE IN REVENUES
Check w/ Alternate Method
[11 empty] | Power Input to Store Lean Solvent (MW): | 42.712
[11 empty] | Energy Output When Discharge Lean Solvent (MW): | 161.8588
[11 empty] | Net Energy Delivered to Grid Decrease When Storing Lean Solvent (MW): | 165.0759
[11 empty] | Net Energy Delivered to Grid From Continuous Regeneration Decreased When Discharging Stored Lean Solvent (MW): | 122.4599
[11 empty] | Net Power Change (MW): | -125.677

## ParameterEstimation650MWHighHR
Determining parameters for base CCS facility and flexible CCS facility using IECM results for a 650 MW gross plant | [6 empty] | This section tests different parameter values in IECM to model flexible CCS
burning sub-bit. or bit. fuel and at constant fuel input. Crucially, heat rate here is set to roughly 10,000 Btu/kWh. | [6 empty] | operations while discharging stored lean solvent. These values are then used in IECM
BASE PLANT |  | CCS Plant |  |  |  |  | to generate the 'CCS, Discharging Stored Lean Solvent' plant in blue area at left. |  |  |  | TESTING RELATIONSHIP BETWEEN CO2 CAPTURE SYSTEM USE AND REGENERATOR USE (ALL IN MW)
Control techs: |  | Same as base plant plus amine system | [5 empty] | TESTING SOLVENT STORAGE DISCHARGING |  |  | I want to know what the relationship in energy demanded by the regenerator and the rest of the CO2 capture system is.
In-Furnace NOx Controls | [7 empty] | For plant w/ CCS @ 650 MW gross output & bituminous fuel |  |  | The rest of the CO2 capture system's energy use is available in the CO2 Capture System Use field, already provided in MW.
Hot-Side SCR |  | CCS Plant w/ Solvent Storage | [5 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | The regenerator energy demand, in MWh, can be determined by taking the difference in the net output of a coal plant
Cold-Side ESP |  | Model as CCS plant while discharging stored lean solvent. | [5 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | w/out and w/ CCS (which embodies the entire energy demand by capturing CO2) and subtracting the CO2 Capture System Use
Wet FGD |  | See tables at right for parameter values to model generation while discharging | [5 empty] | Capture, Regen. Heat Requirement | 1523 | 0.01 | value.
Carbon Injection |  |  | stored lean solvent. |  |  |  |  | Performance, Amine Scrubber Power Req | 11.7 | 1
Once-Through Cooling | [10 empty] | Data is for base vs. CCS plant, defined at left, with bituminous coal.
Boiler Efficiency: 70% | [7 empty] | For plant w/ CCS @ 650 MW gross output & subbituminous fuel
Coal type: | [7 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | Base Plant Gross Output (MW) | Base Plant Net Output (MW) | Base Plant Fuel Input (tons/hr) | CCS Plant Fuel Input (tons/hr) | CCS Plant Gross Output (MW) | CCS Plant Net Output (MW) | CCS Plant CO2 Capture System Use (MW) | Base-CCS Net Output (MW) | CCS Plant Implied Regenerator Energy Use (MW) | Regenerator Energy Use / CO2 Capture System Use (MW/MW)
Subbit: Wyoming PRB | [7 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | 650 | 610 | 261.2 | 261.2 | 510.6 | 407.1 | 59.74 | 202.9 | 143.16 | 2.3964
Bit: Appalachian Low-Sulfur | [7 empty] | Capture, Regen. Heat Requirement | 1514 | 0.01
[8 empty] | Performance, Amine Scrubber Power Req | 7.928 | 0.8
Plant | Fuel Input (tons/hr) | Gross Output (MW) | Net Output (MW) | CO2 Capture System Use (MW) | Solvent Flow Rate (tons/hr) | [13 empty] | Mean: | 2.3964
Subbituminous Coal
Base | [5 empty] | Capac Pen, Base -> CCS (%)
CCS
CCS, Discharging Stored Lean Solvent
Bituminous Coal
Base | 261.2 | 650 | 610 | 0 | 0 | Capac Pen, Base -> CCS (%)
CCS | 261.2 | 510.6 | 407.1 | 59.74 | 9541 | 0.33262
CCS, Discharging Stored Lean Solvent | 261.2 | 650 | 594.3 | 6.5 | 9541
Parameter Estimates
Value | Units | Parameter
Subbituminous Coal
Continuous (Normal) CCS Operations
0 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
#DIV/0! | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
#DIV/0! | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
#DIV/0! | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator) [constant 'd' in slide 9 on accompanying slide deck]
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
0 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
#DIV/0! | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS Operations While Discharging Stored Lean Solvent
#DIV/0! | MWh/tons | Incremental net energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent used.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
#DIV/0! | MWh/MWh | Incremental net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
[Constant 'Y' on slide 17 in accompanying slide deck]
#DIV/0! | tons/MWh | Net Heat Rate = Fuel In / Net Grid Output
Determining Extra Solvent Needed to Capture CO2 from Fuel Used to Regenerate Stored Lean Solvent
#DIV/0! | tons fuel / MWh | Gross Heat Rate = Fuel In / (Gross Output) = Fuel In / (Pgrid + Pco2 + Pregen)
[This includes energy to the regenerator!]
Convert value to tons fuel to provide energy to regenerate solvent / tons solvent using MWh energy input required to regenerate 1 ton of solvent
#DIV/0! | tons fuel / ton solvent regenerated
Using that value, know for each ton of to-be-stored lean solvent want to regenerate, how many tons of fuel required
|  | Ex: | 1 | to-be-stored tons of lean solvent
|  |  | #DIV/0! | required tons of fuel
Now need to know additional fuel input to capture CO2 from fuel used to regenerate to-be-stored lean solvent
To know that, need to know how many tons of solvent is required to capture CO2 emissions from some amount of fuel input
#DIV/0! | tons solvent / ton fuel's co2 emissions
So, need ~24 tons of solvent to capture CO2 emissions from a single ton of fuel input
Multiplying required fuel to get to-be-stored lean solvent by tons solvent necessary to capture co2 from some amount of fuel input, can get extra tons of solvent needed per ton of to-be-stored-lean-solvent regenerated
#DIV/0! | ton extra solvent necessary / ton solvent to be stored regenerated
And we know how much MWh required to regenerate 1 ton of solvent, so can get a MWh value for that solvent
#DIV/0! | MWh for extra solvent / ton solvent to be stored regenerated
And I know how much energy it takes to regenerate one ton of to-be-stored solvent, so I can calculate the ratio of MWh for extra solvent to MWh for to-be-stored solvent
#DIV/0! | MWh for extra solvent / MWh for solvent to be regenerated
[since using same MWh/ton solvent ratio for numerator and denominator, above value is the value as 'ton extra solvent / ton solvent ot be regenerated' value[
Value | Units | Parameter
Bituminous Coal
Continuous (Normal) CCS Operations
202.9 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
47.0232 | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
0.042668 | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
2.0064 | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator) [constant 'd' in slide 9 on accompanying slide deck]
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
143.16 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
66.6457 | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS Operations While Discharging Stored Lean Solvent
0.062289 | MWh/tons | Incremental et energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent discharged.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
2.929 | MWh/MWh | Net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
Know that for every ton stored lean solvent discharged, can generate 0.07 MWh.
[Constant 'Y' on slide 17 in accompanying slide deck]
0.43951 | tons/MWh | Net Heat Rate = Fuel In / Net Grid Output
Determining Extra Solvent Needed to Capture CO2 from Fuel Used to Regenerate Stored Lean Solvent
0.4282 | tons fuel / MWh | Gross Heat Rate = Fuel In / (Gross Output) = Fuel In / (Pgrid + Pco2 + Pregen)
[This includes energy to the regenerator!]
Convert value to tons fuel to provide energy to regenerate solvent / tons solvent using MWh energy input required to regenerate 1 ton of solvent
0.0091061 | tons fuel / ton solvent regenerated
Using that value, know for each ton of to-be-stored lean solvent want to regenerate, how many tons of fuel required
|  | Ex: | 1 | to-be-stored tons of lean solvent
|  |  | 0.0091061 | required tons of fuel
Now need to know additional fuel input to capture CO2 from fuel used to regenerate to-be-stored lean solvent
To know that, need to know how many tons of solvent is required to capture CO2 emissions from some amount of fuel input
36.5276 | tons solvent / ton fuel's co2 emissions |  | [this assumes that part of fuel input is used to generate that lean]
So, need ~24 tons of solvent to capture CO2 emissions from a single ton of fuel input
Now get extra tons of solvent needed per ton of to-be-stored-lean-solvent regenerated - see calculation steps below. Scalar = (X/(1/Z-X)).
0.4984 | ton extra solvent necessary / ton solvent to be stored regenerated |  |  |  | [SEE CALCULATION STEPS BELOW]
And we know how much MWh required to regenerate 1 ton of solvent, so can get a MWh value for that solvent
0.010599 | MWh for extra solvent / ton solvent to be stored regenerated
And I know how much energy it takes to regenerate one ton of to-be-stored solvent, so I can calculate the ratio of MWh for extra solvent to MWh for to-be-stored solvent
0.4984 | MWh for extra solvent / MWh for solvent to be regenerated
[since using same MWh/ton solvent ratio for numerator and denominator, above value is the value as 'ton extra solvent / ton solvent ot be regenerated' value[
CALCULATION STEPS FOR TON EXTRA SOLVENT / TON SOLVENT TO BE STORED REGENERATED
X = tons fuel / ton solvent regenerated
Z = tons solvent / ton fuel's CO2 emissions
A = amount of extra solvent regenerated to capture CO2 emissions from fuel used to regenerate to-be-stored lean solvent
B = amount of to-be-stored lean solvent regenerated
Total Fuel Consumption = X*A + X*B
Only A captures CO2 emissions, not B. So - how much B is necessary to capture CO2?
B*(1/Z) = quantity of fuel from which CO2 emissions are captured by B
Quantity of fuel from which CO2 emissions must be captured is entire fuel input for A and B (since A does not contribute at all to capturing CO2). Thus:
B* (1/Z) = Total Fuel Consumption = X*A + X*B
B*(1/Z-X) = X*A
B=X*A/(1/Z-X)
B=(X/(1/Z-X))*A
So the relevant scalar between extra solvent needed to capture CO2 from fuel used to generate to-be-stored lean solvent is:
X/(1/Z-X))

## NumericExample650MWHighHR
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  |  | 4 time steps: | [7 empty] | Same Example Using My Modeling Scheme
Uses a high heat rate! |  |  |  |  | t=0: max generation | [7 empty] | Base CCS Plant
Plant specification: CCS plant type on 'ParameterEstimation650MWHighHR' sheet, bituminous coal |  |  |  |  | t=1: store lean solvent (fully charge lean solvent tank) | [7 empty] | 455 | Net Capacity w/ CCS (MW) |  |  |  | **Note that these values ARE not the same as numeric value to left because of different storage amounts.
Plant Parameters w/ CCS |  |  |  |  | t=2: max generation | [7 empty] | 613.7 | Pre-CCS Net Capacity (MW) |  |  |  | **However, if you scale based on energy to continuous solvent regeneration, results are the same.
Value | Ref to Prior Sheet (for reference) |  |  |  | t=3: max generation utilizing stored lean solvent | t= | 0 | 1 | 2 | 3 |  |  | 11% | Heat Rate Penalty |  |  |  |  | t= | 0 | 1 | 2 | 3
455 | 455 | MW | Net output |  |  | Non-flexible CCS | [6 empty] | 25.86% | CCS Capacity Penalty |  |  |  |  | Continuous Gen
158.7 | 158.7 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  |  | Net Power Output to Grid (MW): | 455 | 455 | 455 | 455 |  |  | 14.86% | Regenerator Capacity Penalty |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 455 | 455 | 455
7431 | 7431 | tons | Lean solvent flow rate |  |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 7431 | 7431 | 7431 |  |  | 46.53 | Max Energy Input to CO2 Capture System (MWh) | [8 empty] | 1820 | Total Gen
46.53 | 46.53 | MW | CO2 Capture System Use |  |  | CO2 Capture System Power Use (MW): | 46.53 | 46.53 | 46.53 | 46.53 |  |  | 9.7786 | Net Energy to Grid per Energy Input to CO2 Capture System (MWh/MWh) |  |  |  |  | Use of Stored Solvent, True Pump System
112.17 | . | MW | Regenerator Use |  |  | Regenerator Power Use (MW): | 112.17 | 112.17 | 112.17 | 112.17 |  |  | 20% | Min loading of steam turbine |  |  |  |  | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 188.0438
0.021356 | 0.021356 | MWh/ton | Energy required per ton solvent regenerated |  |  | Total Power Input to Capture CO2 (MW): | 158.7 | 158.7 | 158.7 | 158.7 |  |  | 91 | Min load of steam turbine (MW) |  |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 27.6074 | 0 | 0
0.06123 | 0.06123 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  | Gross Power Output (MW): | 613.7 | 613.7 | 613.7 | 613.7 |  |  | 159.7034 | Tons lean solvent regenerated per unit energy used in CO2 Capture System (tons/MWh) |  |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 18.9226 | 46.53 | 19.2301
0.70681 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator | [6 empty] | 1820 | Total Net Power Delivery to Grid (MW): |  | 0.34833 | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to |  |  |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 19.2301
0.29319 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [6 empty] | 2454.8 | Total Gross Output (MW) |  |  |  | Capture Sys for Stored Lean Solvent (MWh/MWh): |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 9.6166 | 0 | 0
9.7786 | 9.7786 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank | Solvent Storage Generator | [5 empty] | Solvent Regenerated (tons): | 7431 | 7431 | 7431 | 3071.1068
12.1085 | 12.1085 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 455 | 207.3248 | 455 | 271.3101 | [Declines b/c of less continuous solvent regen] | 0 | General Parameters | [5 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 357.2085
[6 empty] | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 242.793 | [Based on discharged amount of stored lean solvent] | 601.3983 | 90% | Heat Rate Penalty Reduction |  |  |  |  | Solvent Flow from Stored Lean Solvent (tons): | 0 | 0 | 0 | 4413.7412
[6 empty] | Total Net Power Output to Grid (MW): | 455 | 207.3248 | 455 | 514.1031 | [Not at max net output because would need full lean solvent tank to get max; see right] | 601.3983 | 95.75% | Capacity Penalty Reduction |  |  | 12.8844 |  | Percent of Continual Solvent Flow Displaced by Stored Solvent (%): | 0 | 0 | 0 | 59.4%
Plant Parameters w/ CCS Using Stored Lean Solvent | [5 empty] | Total Mass Solvent Continuously Regenerated (tons): | 7431 | 4431 | 7431 | 4431 | [Limited by absorber capacity] | 0 | 3.7895 | Net energy output to grid per energy pumped (MWh/MWh) |  |  |  |  | Total Max Capacity, Accounting for % Continual Regeneration Displaced (MW): | 0 | 0 | 0 | 545.2523
Value | Ref to Prior Sheet (for reference) |  |  |  |  | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 7431 | 3386 | 7431 | 4431 | [Manually calculated through iterative procedure; set value to that in prior row ('Total Mass Solvent Continuously Regenerated'), then subtract value below in 'Required Adder to Continuous Lean Solvent' row iteratively until that value = 1.] | 0 |  | [Includes energy to regenerator in denominator] |  |  |  |  | Total Solvent Flow Rate (tons): | 7431 | 7431 | 7431 | 7484.848
601.4 | 601.4 | MW | Net output |  |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 1045 | 0 | 0 | [Discharge entire tank] | 7431 | 12.9389 | Net energy output to grid per energy pumped, excluding energy to regenerator in value this is multiplied with (MWh/MWh) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 27.6074
7431 | 7431 | tons | Lean solvent flow rate |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 3000 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 7431 |  | equals prior parameter*(1+Eregen/Eco2capturesystem) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 329.6011
4.55 | 4.55 | MW | CO2 Capture System Use |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3000 |  | 7431 | 606.9493 | Max total (Base + SS) achievable capcaity (MW) |  |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 545.2523
0 | . | MW | Regenerator Use |  |  | Mass of Solvent Passed Through Absorber (tons): | 7431 | 4431 | 7431 | 7431 |  | 0 | [10 empty] | 1546.2523 | Total Gen
3000 | . | tons | Lean and rich solvent tank size |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 3000 | 0 | 0 | 3000 |  | 0 | I model solvent storage generator as additional stand-alone generator, w/ only incremental generation to base CCS facility. | [9 empty] | -0.15041 | Percent Change in Gen w/ Flex CCS vs. Nonflex CCS
3000 | . | tons | Initial mass of stored rich solvent |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 3000 | 3000 | 0 |  | 0 | But solvent storage generator really should replace generation from base CCS facility. | [5 empty] | Use of Stored Solvent, Incremental Pump System
0 | . | tons | Initial mass of stored lean solvent |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 158.6964 | 94.6284 | 158.6964 | 94.6284 |  | 0 | When I have full pump load at my stand alone generator, need to inflate this value to scale from incremental pump system | [5 empty] | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 455
0.021356 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 46.529 | 27.7446 | 46.529 | 27.7446 |  | 0 | to true pump system. | [5 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 6.9115 | 0 | 0
0.080931 | 0.080931 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 112.1675 | 66.8839 | 112.1675 | 66.8839 |  | 0 | True Pump System | [5 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 18.9226 | 46.53 | 46.53
3.7895 | 3.7895 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 6.5432 | 0 | 0 |  |  | 27.6074 | Max Capacity (MW) |  | [Excludes energy to regenerator] |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 46.53 | 9.306 | 46.53 | 46.53
64.068 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 64.068 | 0 | 0 |  | 0 |  | [Steam turbine min load defined as 20%, so must |  |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 9.6166 | 0 | 0
[6 empty] | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 18.7844 | 0 | 0 |  | 0 |  | maintain 20% load through continuous solvent regeneration.] |  |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 89.4269
[6 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 45.2836 | 0 | 0 |  | 0 | 7499.5898 | Tank size to meet max possible output using stored lean solvent (tons) |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 6.9115
[6 empty] | CO2 Capture System Power Use, Total (MW): | 46.529 | 46.529 | 46.529 | 27.7446 |  | 0 | 4408.9988 | Solvent pumped at max pump capacity (tons) |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 82.5154
[6 empty] | Regenerator Power Use, Total (MW): | 112.1675 | 112.1675 | 112.1675 | 66.8839 |  |  |  |  | [Pump max capacity above does not include energy for regenerator.] |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 544.4269
|  |  |  | 3386 |  | Total Power Input to Capture CO2 (MW): | 158.6964 | 158.6964 | 158.6964 | 94.6284 |  |  |  |  | [~80% of tank size can be filled in 1 hour, which makes sense given 20% min load on ST.] | [7 empty] | 1545.4269 | Total Gen
[6 empty] | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 613.6964 | 366.0212 | 613.6964 | 608.7316 |  |  | 58.79% | Percent of solvent necessary for max output that can be stored in 1 hour
[6 empty] | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 7430.9556 | 4431.9752 | 7430.9556 | NA | [8 empty] | IGNORE THIS BOX
[6 empty] | Required Adder to Continuous Lean Solvent (tons): | -0.044431 | 0.97521 | -0.044431 | NA |  |  | Incremental Pump System | [8 empty] | Use of Stored Solvent w/ Backcalculated Regenerator Energy Use
[10 empty] | 1631.4279 | Total Net Power Delivery to Grid (MW) |  | 151.9493 | Max incremental generation w/ stored lean solvent (MW) | [7 empty] | Net Energy Output to Grid (MWh): | 455 | 387.415 | 455 | 455
[10 empty] | -188.5721 | Change in Net Power Delivery to Grid |  | 1877.5166 | Volume of stored lean solvent for max inc. gen (tons) | [7 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 6.9115 | 0 | 0 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[12 empty] | from Cont. Nonflex CCS ops | 40.0962 | Max capacity (MW), based on volume of stored lean solven | [7 empty] | Back-calculated Regenerator Energy Use to Store Lean Solvent (MWh): | 0 | 66.6543 | 0 | 0
[10 empty] | -10.36% | % Change in Net Power Output |  |  |  | necessary for max incremental gen above. | [6 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 39.6185 | 46.53 | 46.53 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[6 empty] | Ratio of E to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.25859 | 0.25853 | 0.25859 | NA |  |  |  |  | [Includes energy to regenerator.] | [6 empty] | Back-calculated Regenerator Energy Use for Continuous Regeneration (MWh): | 112.3402 | 95.6534 | 112.3402 | 112.3402
[6 empty] | Ratio of E to CO2 Capture System to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.075818 | 0.0758 | 0.075818 | NA |  |  | 11.7563 | Max capacity (MW), excluding energy to regenerator. | [7 empty] | Tons Lean Solvent Stored (tons): | 0 | 3444.736 | 0 | 0
[6 empty] | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to Capture Sys for Stored Lean Solvent (MWh/MWh): | NA | 0.34833 | NA | NA |  |  | 6.9115 | Max capacity (MW), excluding energy to regenerator and accounting for limit on how much true pump system can be filled in 1 hour. | [7 empty] | Tons Solvent Continuously Regenerated (tons): | 7439.1386 | 6334.1402 | 7439.1386 | 7439.1386
[13 empty] | 3.9944 | Ratio of pump max capacity in incremental vs. true system | [7 empty] | Tons Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3444.736
[13 empty] | 39.06 | Reduction in base CCS net output per unit energy used to pump lean solvent for storage (MWh/MWh) | [7 empty] | Net Energy to Grid, Tons Continuously Regenerated (MWh): | 455.4985 | 387.8394 | 455.4985 | 455.4985
[6 empty] | Diff in Net Pow Output from Continuous CCS Operations (MW:) | 0 | -247.6752 | 0 | 59.1031 |  |  | 185.0373 | Max capacity of base CCS facility at max pump capacity (MW) | [7 empty] | Net Energy to Grid, Tons Stored Lean Discharged (MWh): | 0 | 0 | 0 | 278.7859 | 278.7805
[6 empty] | Price ($/MWh): | 0 | 10 | 0 | 42 |  |  |  | Check: should be 20% of capacity of base CCS facility | [8 empty] | 613.8702 | 596.2527 | 613.8702 | 613.8702
[6 empty] | Change in Revenues ($): | 0 | -2476.7522 | 0 | 2482.3315 |  |  |  |  | 91 | [6 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 278.7805
[10 empty] | 5.5793 | TOTAL CHANGE IN REVENUES | [10 empty] | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 27.6074
[13 empty] | Extra Generation Unit | [8 empty] | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 251.1731
[10 empty] | Check w/ Alternate Method |  |  | 145.0378 | Max Capacity (MW) | [7 empty] | Total Generation (MWh): | 455 | 380.5035 | 455 | 733.7805
[10 empty] | Power Input to Store Lean Solvent (MW): | 64.068 |  | 20.985 | Ratio of generation at extra generating unit to generation at pumping unit (MW/MW) | [11 empty] | 2024.284 | Total Gen
[10 empty] | Energy Output When Discharge Lean Solvent (MW): | 242.7882
[10 empty] | Net Energy Delivered to Grid Decrease When Storing Lean Solvent (MW): | 247.6752
[10 empty] | Net Energy Delivered to Grid From Continuous Regeneration Decreased When Discharging Stored Lean Solvent (MW): | 183.6899
[10 empty] | Net Power Change (MW): | -188.5768

## ParameterEstimation650MWMidHR
Determining parameters for base CCS facility and flexible CCS facility using IECM results for a 650 MW gross plant | [6 empty] | This section tests different parameter values in IECM to model flexible CCS
burning sub-bit. or bit. fuel and at constant fuel input. Crucially, heat rate here is set to roughly 10,000 Btu/kWh. | [6 empty] | operations while discharging stored lean solvent. These values are then used in IECM
BASE PLANT |  | CCS Plant |  |  |  |  | to generate the 'CCS, Discharging Stored Lean Solvent' plant in blue area at left. | [5 empty] | TESTING RELATIONSHIP BETWEEN CO2 CAPTURE SYSTEM USE AND REGENERATOR USE (ALL IN MW)
Control techs: |  | Same as base plant plus amine system | [7 empty] | TESTING SOLVENT STORAGE DISCHARGING |  |  | I want to know what the relationship in energy demanded by the regenerator and the rest of the CO2 capture system is.
In-Furnace NOx Controls | [9 empty] | For plant w/ CCS @ 650 MW gross output & bituminous fuel |  |  | The rest of the CO2 capture system's energy use is available in the CO2 Capture System Use field, already provided in MW.
Hot-Side SCR |  | CCS Plant w/ Solvent Storage | [7 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | The regenerator energy demand, in MWh, can be determined by taking the difference in the net output of a coal plant
Cold-Side ESP |  | Model as CCS plant while discharging stored lean solvent. | [7 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | w/out and w/ CCS (which embodies the entire energy demand by capturing CO2) and subtracting the CO2 Capture System Use
Wet FGD |  | See tables at right for parameter values to model generation while discharging | [7 empty] | Capture, Regen. Heat Requirement | 1523 | 0.01 | value.
Carbon Injection |  |  | stored lean solvent. | [6 empty] | Performance, Amine Scrubber Power Req | 9.901 | 0.9
Once-Through Cooling | [12 empty] | Data is for base vs. CCS plant, defined at left, with bituminous coal.
Boiler Efficiency: 80% | [9 empty] | For plant w/ CCS @ 650 MW gross output & subbituminous fuel
Coal type: | [9 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | Base Plant Gross Output (MW) | Base Plant Net Output (MW) | Base Plant Fuel Input (tons/hr) | CCS Plant Fuel Input (tons/hr) | CCS Plant Gross Output (MW) | CCS Plant Net Output (MW) | CCS Plant CO2 Capture System Use (MW) | Base-CCS Net Output (MW) | CCS Plant Implied Regenerator Energy Use (MW) | Regenerator Energy Use / CO2 Capture System Use (MW/MW)
Subbit: Wyoming PRB | [9 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | 650 | 612.1 | 228.6 | 228.6 | 528.2 | 434.4 | 52.29 | 177.7 | 125.41 | 2.3984
Bit: Appalachian Low-Sulfur | [9 empty] | Capture, Regen. Heat Requirement | 1514 | 0.01
[10 empty] | Performance, Amine Scrubber Power Req | 7.928 | 0.8
Plant | Fuel Input (tons/hr) | Gross Output (MW) | Net Output (MW) | CO2 Capture System Use (MW) | Solvent Flow Rate (tons/hr) | [15 empty] | Mean: | 2.3984
Subbituminous Coal
Base | [5 empty] | Capac Pen, Base -> CCS (%)
CCS
CCS, Discharging Stored Lean Solvent
Bituminous Coal
Base | 228.6 | 650 | 612.1 | 0 | 0 | Capac Pen, Base -> CCS (%)
CCS | 228.6 | 528.2 | 434.4 | 52.29 | 8351 | 0.29031 |  | 0.37347 | 13080 | HV |  | 528 MW excludes the regenerator load
CCS, Discharging Stored Lean Solvent | 228.6 | 650 | 597.8 | 5.85 | 8348 |  |  |  | 9.7699 | MMBtu/MWh
Parameter Estimates | [7 empty] | 0.52624
Value | Units | Parameter | [6 empty] | 13.7665 | MMBtu/MWh
Subbituminous Coal | [8 empty] | 0.40907
Continuous (Normal) CCS Operations | [8 empty] | 13.6779
0 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
#DIV/0! | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
#DIV/0! | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
#DIV/0! | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator) [constant 'd' in slide 9 on accompanying slide deck]
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
0 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
#DIV/0! | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS Operations While Discharging Stored Lean Solvent
#DIV/0! | MWh/tons | Incremental net energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent used.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
#DIV/0! | MWh/MWh | Incremental net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
[Constant 'Y' on slide 17 in accompanying slide deck]
#DIV/0! | tons/MWh | Net Heat Rate = Fuel In / Net Grid Output
Determining Extra Solvent Needed to Capture CO2 from Fuel Used to Regenerate Stored Lean Solvent
#DIV/0! | tons fuel / MWh | Gross Heat Rate = Fuel In / (Gross Output) = Fuel In / (Pgrid + Pco2 + Pregen)
[This includes energy to the regenerator!]
Convert value to tons fuel to provide energy to regenerate solvent / tons solvent using MWh energy input required to regenerate 1 ton of solvent
#DIV/0! | tons fuel / ton solvent regenerated
Using that value, know for each ton of to-be-stored lean solvent want to regenerate, how many tons of fuel required
|  | Ex: | 1 | to-be-stored tons of lean solvent
|  |  | #DIV/0! | required tons of fuel
Now need to know additional fuel input to capture CO2 from fuel used to regenerate to-be-stored lean solvent
To know that, need to know how many tons of solvent is required to capture CO2 emissions from some amount of fuel input
#DIV/0! | tons solvent / ton fuel's co2 emissions
So, need ~24 tons of solvent to capture CO2 emissions from a single ton of fuel input
Multiplying required fuel to get to-be-stored lean solvent by tons solvent necessary to capture co2 from some amount of fuel input, can get extra tons of solvent needed per ton of to-be-stored-lean-solvent regenerated
#DIV/0! | ton extra solvent necessary / ton solvent to be stored regenerated
And we know how much MWh required to regenerate 1 ton of solvent, so can get a MWh value for that solvent
#DIV/0! | MWh for extra solvent / ton solvent to be stored regenerated
And I know how much energy it takes to regenerate one ton of to-be-stored solvent, so I can calculate the ratio of MWh for extra solvent to MWh for to-be-stored solvent
#DIV/0! | MWh for extra solvent / MWh for solvent to be regenerated
[since using same MWh/ton solvent ratio for numerator and denominator, above value is the value as 'ton extra solvent / ton solvent ot be regenerated' value[
Value | Units | Parameter
Bituminous Coal
Continuous (Normal) CCS Operations
177.7 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
46.9949 | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
0.052018 | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
2.4446 | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator) [constant 'd' in slide 9 on accompanying slide deck]
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
125.41 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
66.5896 | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS Operations While Discharging Stored Lean Solvent
0.07161 | MWh/tons | Incremental et energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent discharged.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
3.3653 | MWh/MWh | Net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
Know that for every ton stored lean solvent discharged, can generate 0.07 MWh.
[Constant 'Y' on slide 17 in accompanying slide deck]
0.3824 | tons/MWh | Net Heat Rate = Fuel In / Net Grid Output
Determining Extra Solvent Needed to Capture CO2 from Fuel Used to Regenerate Stored Lean Solvent
0.37347 | tons fuel / MWh | Gross Heat Rate = Fuel In / (Gross Output) = Fuel In / (Pgrid + Pco2 + Pregen)
[This includes energy to the regenerator!]
Convert value to tons fuel to provide energy to regenerate solvent / tons solvent using MWh energy input required to regenerate 1 ton of solvent
0.007947 | tons fuel / ton solvent regenerated
Using that value, know for each ton of to-be-stored lean solvent want to regenerate, how many tons of fuel required
|  | Ex: | 1 | to-be-stored tons of lean solvent
|  |  | 0.007947 | required tons of fuel
Now need to know additional fuel input to capture CO2 from fuel used to regenerate to-be-stored lean solvent
To know that, need to know how many tons of solvent is required to capture CO2 emissions from some amount of fuel input
36.5311 | tons solvent / ton fuel's co2 emissions |  | [this assumes that part of fuel input is used to generate that lean]
So, need ~24 tons of solvent to capture CO2 emissions from a single ton of fuel input
Now get extra tons of solvent needed per ton of to-be-stored-lean-solvent regenerated - see calculation steps below. Scalar = (X/(1/Z-X)).
0.40907 | ton extra solvent necessary / ton solvent to be stored regenerated |  |  |  | [SEE CALCULATION STEPS BELOW]
And we know how much MWh required to regenerate 1 ton of solvent, so can get a MWh value for that solvent
0.0087046 | MWh for extra solvent / ton solvent to be stored regenerated
And I know how much energy it takes to regenerate one ton of to-be-stored solvent, so I can calculate the ratio of MWh for extra solvent to MWh for to-be-stored solvent
0.40907 | MWh for extra solvent / MWh for solvent to be regenerated
[since using same MWh/ton solvent ratio for numerator and denominator, above value is the value as 'ton extra solvent / ton solvent ot be regenerated' value[
CALCULATION STEPS FOR TON EXTRA SOLVENT / TON SOLVENT TO BE STORED REGENERATED
X = tons fuel / ton solvent regenerated
Z = tons solvent / ton fuel's CO2 emissions
A = amount of extra solvent regenerated to capture CO2 emissions from fuel used to regenerate to-be-stored lean solvent
B = amount of to-be-stored lean solvent regenerated
Total Fuel Consumption = X*A + X*B
Only A captures CO2 emissions, not B. So - how much B is necessary to capture CO2?
B*(1/Z) = quantity of fuel from which CO2 emissions are captured by B
Quantity of fuel from which CO2 emissions must be captured is entire fuel input for A and B (since A does not contribute at all to capturing CO2). Thus:
B* (1/Z) = Total Fuel Consumption = X*A + X*B
B*(1/Z-X) = X*A
B=X*A/(1/Z-X)
B=(X/(1/Z-X))*A
So the relevant scalar between extra solvent needed to capture CO2 from fuel used to generate to-be-stored lean solvent is:
X/(1/Z-X))

## ParamsAcrossHRs650MW
This sheet collects parameter estimates for 650 MW gross facilities at different heat rates to see what relationship, if any, exists between heat rate and parameter values.
Heat Rate (given as boiler eff) | PARAMETERS
70%
80%
90%

## ParameterEstimation450MWPlant
BASE PLANT |  | CCS Plant |  |  |  |  | TESTING SOLVENT STORAGE DISCHARGING |  |  | TESTING RELATIONSHIP BETWEEN CO2 CAPTURE SYSTEM USE AND REGENERATOR USE (ALL IN MW)
Control techs: |  | Same as base plant plus amine system |  |  |  |  | For plant w/ CCS @ 450 MW gross output & bituminous fuel |  |  | I want to know what the relationship in energy demanded by the regenerator and the rest of the CO2 capture system is.
In-Furnace NOx Controls | [6 empty] | Field | Default Value | Stored Lean Solvent Discharge Config | The rest of the CO2 capture system's energy use is available in the CO2 Capture System Use field, already provided in MW.
Hot-Side SCR |  | CCS Plant w/ Solvent Storage |  |  |  |  | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | The regenerator energy demand, in MWh, can be determined by taking the difference in the net output of a coal plant
Cold-Side ESP |  | Model as CCS plant while discharging stored lean solvent. |  |  |  |  | Capture, Regen. Heat Requirement | 1523 | 0.01 | w/out and w/ CCS (which embodies the entire energy demand by capturing CO2) and subtracting the CO2 Capture System Use
Wet FGD |  | See tables at right for parameter values to model generation while discharging |  |  |  |  | Performance, Amine Scrubber Power Req | 8.595 | 0.85 | value.
Carbon Injection |  |  | stored lean solvent.
Once-Through Cooling | [6 empty] | For plant w/ CCS @ 450 MW gross output & subbituminous fuel |  |  | Data is for base vs. CCS plant, defined at left, with bituminous coal.
Coal type: | [6 empty] | Field | Default Value | Stored Lean Solvent Discharge Config
Subbit: Wyoming PRB | [6 empty] | T&S Config, CO2 Unit Compression Energy | 84.38 | 8.4 | Base Plant Gross Output (MW) | Base Plant Net Output (MW) | Base Plant Fuel Input (tons/hr) | CCS Plant Fuel Input (tons/hr) | CCS Plant Gross Output (MW) | CCS Plant Net Output (MW) | CCS Plant CO2 Capture System Use (MW) | Base-CCS Net Output (MW) | CCS Plant Implied Regenerator Energy Use (MW) | Regenerator Energy Use / CO2 Capture System Use (MW/MW)
Bit: Appalachian Low-Sulfur | [6 empty] | Capture, Regen. Heat Requirement | 1514 | 0.01 | 650 | 613.7 | 203.4 | 203.4 | 514.4 | 455 | 46.53 | 158.7 | 112.17 | 2.4107
[7 empty] | Performance, Amine Scrubber Power Req | 9.708 | 0.97 | 500 | 471.9 | 156.5 | 156.5 | 416.4 | 349.7 | 35.79 | 122.2 | 86.41 | 2.4144
[10 empty] | 400 | 377.3 | 125.2 | 125.2 | 333.1 | 279.6 | 28.63 | 97.7 | 69.07 | 2.4125
Plant | Fuel Input (tons/hr) | Gross Output (MW) | Net Output (MW) | CO2 Capture System Use (MW) | Solvent Flow Rate (tons/hr)
Subbituminous Coal
Base | 231.7 | 450 | 418.8 | 0 | 0 | Capac Pen (%)
CCS | 231.7 | 367.6 | 298.6 | 35.69 | 5642 | 0.28701
CCS, Using Stored Lean Solvent | 231.7 | 450 | 408 | 4.365 | 5641
Bituminous Coal
Base | 140.9 | 450 | 424.6 | 0 | 0 | Capac Pen (%)
CCS | 140.9 | 374.9 | 314.8 | 32.22 | 5146 | 0.2586
CCS, Using Stored Lean Solvent | 140.9 | 450 | 415.4 | 3.825 | 5145
Parameter Estimates
Value | Units | Parameter
Subbituminous Coal
Continuous/normal CCS operations
120.2 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
46.9384 | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
0.052924 | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
2.4842 | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator)
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
84.51 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
66.7613 | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS operations using stored lean solvent
0.072328 | MWh/tons | Net energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent used.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
3.3949 | MWh/MWh | Net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
Know that for every ton stored lean solvent discharged, can generate 0.07 MWh.
Value | Units | Parameter
Bituminous Coal
Continuous/normal CCS operations
109.8 | MW | Change in Net MW when retrofit CCS = MW used to run CO2 capture system (including regenerator)
46.867 | tons/MWh | Solvent flow rate per unit energy sent to CO2 capture
Note that this includes steam energy input to regenerator, represented in MWh
0.061174 | MWh/tons | Net energy delivered to grid per unit of lean solvent regenerated.
2.867 | MWh/MWh | Net energy delivered to grid per unit energy used in CO2 capture system (including regenerator)
In other words, every MWh used to capture CO2 enables 2.48 MWh delivered to grid.
77.58 | MWh | Regenerator size, in terms of steam energy input (in units of MWh equivalent)
This tells me throughput of regenerator when "right-sized", i.e. sized to CCS plant at maximum normal operations
66.3315 | tons/MWh | Solvent flow rate per unit energy sent to regenerator only (not to rest of CO2 capture system).
CCS operations using stored lean solvent
0.080739 | MWh/tons | Incremental et energy delivered to grid while discharging stored lean solvent per unit of stored lean solvent discharged.
Note that this parameter value is greater than that for normal CCS operations (see above), as expected given elimination of most of parasitic load of CO2 capture system while using stored lean solvent.
3.784 | MWh/MWh | Net energy delivered to grid using stored lean solvent per unit of energy input to CO2 capture system to generate requisite amount of stored lean solvent
Know that for every ton stored lean solvent discharged, can generate 0.07 MWh.

## NumericExampleV2MW450
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  |  | 4 time steps: | [8 empty] | Same Example Using My Modeling Scheme
[6 empty] | t=0: max generation | [7 empty] | Base CCS Plant
Plant specification: CCS plant type on prior sheet, bituminous coal | [5 empty] | t=1: store lean solvent (fully charge lean solvent tank) | [7 empty] | 314.8 | Max Net Capacity (MW) |  |  | **Note that these values ARE not the same as numeric value to left because of different storage amounts.
Plant Parameters w/ CCS | [5 empty] | t=2: max generation | [7 empty] | 424.6 | Pre-CCS Net Capacity (MW) |  |  | **However, if you scale based on energy to continuous solvent regeneration, results are the same.
Value | Ref to Prior Sheet (for reference) |  |  |  |  | t=3: max generation utilizing stored lean solvent | [7 empty] | 11% | Heat Rate Penalty |  |  |  | t= | 0 | 1 | 2 | 3
314.8 | 314.8 | MW | Net output | [10 empty] | 25.86% | CCS Capacity Penalty |  |  |  | Continuous Gen
109.8 | 109.8 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  |  |  | t= | 0 | 1 | 2 | 3 |  |  | 14.86% | Regenerator Capacity Penalty |  |  |  | Net Energy Output to Grid (MWh): | 314.8 | 314.8 | 314.8 | 314.8
5146 | 5146 | tons | Lean solvent flow rate |  |  |  | Non-flexible CCS | [6 empty] | 32.22 | Max Energy Input to CO2 Capture System (MWh) | [7 empty] | 1259.2 | Total Gen
32.22 | 32.22 | MW | CO2 Capture System Use |  |  |  | Net Power Output to Grid (MW): | 314.8 | 314.8 | 314.8 | 314.8 |  |  | 9.7703 | Net Energy to Grid per Energy Input to CO2 Capture System (MWh/MWh) |  |  |  | Use of Stored Solvent, True Pump System
77.58 | . | MW | Regenerator Use |  |  |  | Mass Solvent Continuously Regenerated (tons): | 5146 | 5146 | 5146 | 5146 |  |  | 20% | Min loading of steam turbine |  |  |  | Net Energy Output to Grid (MWh): | 314.8 | 62.96 | 314.8 | 130.3074
0.021337 | 0.021337 | MWh/ton | Energy required per ton solvent regenerated |  |  |  | CO2 Capture System Power Use (MW): | 32.22 | 32.22 | 32.22 | 32.22 |  |  | 62.96 | Min load of steam turbine (MW) |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 19.1169 | 0 | 0
0.061174 | 0.061174 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  |  | Regenerator Power Use (MW): | 77.58 | 77.58 | 77.58 | 77.58 |  |  | 159.7145 | Tons lean solvent regenerated per unit energy used in CO2 Capture System (tons/MWh) |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 32.22 | 13.1031 | 32.22 | 13.337
0.70656 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator |  |  |  | Total Power Input to Capture CO2 (MW): | 109.8 | 109.8 | 109.8 | 109.8 |  |  | 0.34833 | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to |  |  |  | E to Continuous Solvent Regen for E to Grid (MWh): | 32.22 | 6.444 | 32.22 | 13.337
0.29344 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [7 empty] | 1259.2 | Total Net Power Delivery to Grid (MW): |  |  |  | Capture Sys for Stored Lean Solvent (MWh/MWh): |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 6.6591 | 0 | 0
9.7703 | 9.7703 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank | Solvent Storage Generator |  |  |  |  | Solvent Regenerated (tons): | 5146 | 5146 | 5146 | 2130.1197
12.1196 | 12.1196 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  |  |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 314.8 | 67.3523 | 314.8 | 131.2788 | [Declines b/c of less continuous solvent regen] | 0 | General Parameters |  |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 246.9883
[7 empty] | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 242.2157 | [Based on discharged amount of stored lean solvent] | 415.4807 | 90% | Heat Rate Penalty Reduction |  |  |  | Solvent Flow from Stored Lean Solvent (tons): | 0 | 0 | 0 | 3059.1108
[7 empty] | Total Net Power Output to Grid (MW): | 314.8 | 67.3523 | 314.8 | 373.4946 | [Not at max net output because would need full lean solvent tank to get max; see right] | 415.4807 | 95.75% | Capacity Penalty Reduction |  |  |  | Percent of Continual Solvent Flow Displaced by Stored Solvent (%): | 0 | 0 | 0 | 59.45%
Plant Parameters w/ CCS Using Stored Lean Solvent | [6 empty] | Total Mass Solvent Continuously Regenerated (tons): | 5146 | 2146 | 5146 | 2146 | [Limited by absorber capacity] | 0 | 3.784 | Net energy output to grid per energy pumped (MWh/MWh) |  |  |  | Total Max Capacity, Accounting for % Continual Regeneration Displaced (MW): | 0 | 0 | 0 | 377.2956
Value | Ref to Prior Sheet (for reference) | [5 empty] | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 5146 | 1101 | 5146 | 2146 |  | 0 |  | [Includes energy to regenerator in denominator] |  |  |  | Total Solvent Flow Rate (tons): | 5146 | 5146 | 5146 | 5189.2305
415.4 | 415.4 | MW | Net output |  |  |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 1045 | 0 | 0 | [Discharge entire tank] | 5146 | 12.9199 | Net energy output to grid per energy pumped, excluding energy to regenerator in value this is multiplied with (MWh/MWh) |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 19.1169
5145 | 5145 | tons | Lean solvent flow rate |  |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 3000 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 5146 |  | equals prior parameter*(1+Eregen/Eco2capturesystem) |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 227.8713
3.825 | 3.825 | MW | CO2 Capture System Use |  |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3000 |  | 5146 | 419.9294 | Max total (Base + SS) achievable capcaity (MW) |  |  |  | Total Net Generation (MWh): | 314.8 | 62.96 | 314.8 | 377.2956
0 | . | MW | Regenerator Use |  |  |  | Mass of Solvent Passed Through Absorber (tons): | 5146 | 2146 | 5146 | 5146 |  | 0 | [9 empty] | 1069.8556 | Total Gen
3000 | . | tons | Lean and rich solvent tank size |  |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 3000 | 0 | 0 | 3000 |  | 0 | I model solvent storage generator as additional stand-alone generator, w/ only incremental generation to base CCS facility. | [8 empty] | -0.15037 | Percent Change in Gen w/ Flex CCS vs. Nonflex CCS
3000 | . | tons | Initial mass of stored rich solvent |  |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 3000 | 3000 | 0 |  | 0 | But solvent storage generator really should replace generation from base CCS facility. |  |  |  |  | Use of Stored Solvent, Incremental Pump System
0 | . | tons | Initial mass of stored lean solvent |  |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 109.8 | 45.7891 | 109.8 | 45.7891 |  | 0 | When I have full pump load at my stand alone generator, need to inflate this value to scale from incremental pump system |  |  |  |  | Net Energy Output to Grid (MWh): | 314.8 | 62.96 | 314.8 | 314.8
0.021337 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 32.22 | 13.4365 | 32.22 | 13.4365 |  | 0 | to true pump system. |  |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 4.7859 | 0 | 0
0.080739 | 0.080739 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 77.58 | 32.3526 | 77.58 | 32.3526 |  | 0 | True Pump System |  |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 32.22 | 13.1031 | 32.22 | 32.22
3.784 | 3.784 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 6.5429 | 0 | 0 |  |  | 19.1169 | Max Capacity (MW) |  | [Excludes energy to regenerator] |  | E to Continuous Solvent Regen for E to Grid (MWh): | 32.22 | 6.444 | 32.22 | 32.22
64.0109 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 64.0109 | 0 | 0 |  | 0 |  | [Steam turbine min load defined as 20%, so must |  |  |  | E to Continuous Solvent Regen for E for Regen Stored Lean Solvent (MWh): | 0 | 6.6591 | 0 | 0
[7 empty] | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 18.7835 | 0 | 0 |  | 0 |  | maintain 20% load through continuous solvent regeneration.] |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 61.8336
[7 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 45.2274 | 0 | 0 |  | 0 | 5201.0996 | Tank size to meet max possible output using stored lean solvent (tons) |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 4.7859
[7 empty] | CO2 Capture System Power Use, Total (MW): | 32.22 | 32.22 | 32.22 | 13.4365 |  | 0 | 3053.2509 | Solvent pumped at max pump capacity (tons) |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 57.0476
[7 empty] | Regenerator Power Use, Total (MW): | 77.58 | 77.58 | 77.58 | 32.3526 |  |  |  |  | [Pump max capacity above does not include energy for regenerator.] |  |  | Total Net Generation (MWh): | 314.8 | 62.96 | 314.8 | 376.6336
[7 empty] | Total Power Input to Capture CO2 (MW): | 109.8 | 109.8 | 109.8 | 45.7891 |  |  |  |  | [~80% of tank size can be filled in 1 hour, which makes sense given 20% min load on ST.] | [6 empty] | 1069.1936 | Total Gen
|  |  |  | 3386 |  |  | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 424.6 | 177.1523 | 424.6 | 419.2837 |  |  | 58.7% | Percent of solvent necessary for max output that can be stored in 1 hour
[7 empty] | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 5146 | 2147.0221 | 5146 | NA
[7 empty] | Required Adder to Continuous Lean Solvent (tons): | 0 | 1.0221 | 0 | NA |  |  | Incremental Pump System | [7 empty] | Use of Stored Solvent w/ Backcalculated Regenerator Energy Use
[11 empty] | 1070.4468 | Total Net Power Delivery to Grid (MW) |  | 105.1294 | Max incremental generation w/ stored lean solvent (MW) | [6 empty] | Net Energy Output to Grid (MWh): | 314.8 | 268.0399 | 314.8 | 314.8
[11 empty] | -188.7532 | Change in Net Power Delivery to Grid |  | 1302.0962 | Volume of stored lean solvent for max inc. gen (tons) | [6 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 4.7859 | 0 | 0 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[12 empty] | from Continuous Non-Flexible CCS Operation |  | 27.7828 | Max capacity (MW), based on volume of stored lean solven | [6 empty] | Back-calculated Regenerator Energy Use to Store Lean Solvent (MWh): | 0 | 46.1552 | 0 | 0
[11 empty] | -17.63% | Change in Net Output as % |  |  |  | necessary for max incremental gen above. | [5 empty] | Energy to Continuous Solvent Regeneration (MWh): | 32.22 | 27.4341 | 32.22 | 32.22 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[7 empty] | Ratio of E to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.2586 | 0.25847 | 0.2586 | NA |  |  |  |  | [Includes energy to regenerator.] | [5 empty] | Back-calculated Regenerator Energy Use for Continuous Regeneration (MWh): | 77.7907 | 66.2358 | 77.7907 | 77.7907
[7 empty] | Ratio of E to CO2 Capture System to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.075883 | 0.075847 | 0.075883 | NA |  |  | 8.1527 | Max capacity (MW), excluding energy to regenerator. | [6 empty] | Tons Lean Solvent Stored (tons): | 0 | 2387.459 | 0 | 0
[7 empty] | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to Capture Sys for Stored Lean Solvent (MWh/MWh): | NA | 0.34833 | NA | NA |  |  | 4.7859 | Max capacity (MW), excluding energy to regenerator and accounting for limit on how much true pump system can be filled in 1 hour. | [6 empty] | Tons Solvent Continuously Regenerated (tons): | 5155.8763 | 4390.0273 | 5155.8763 | 5155.8763
[14 empty] | 3.9944 | Ratio of pump max capacity in incremental vs. true system | [6 empty] | Tons Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 2387.459
[14 empty] | 39.0267 | Reduction in base CCS net output per unit energy used to pump lean solvent for storage (MWh/MWh) | [6 empty] | Net Energy to Grid, Tons Continuously Regenerated (MWh): | 315.4042 | 268.5543 | 315.4042 | 315.4042
[7 empty] | Diff in Net Pow Output from Continuous CCS Operations (MW:) | 0 | -247.4477 | 0 | 58.6946 |  |  | 128.0213 | Max capacity of base CCS facility at max pump capacity (MW) | [6 empty] | Net Energy to Grid, Tons Stored Lean Discharged (MWh): | 0 | 0 | 0 | 192.7601 | 192.7601
[7 empty] | Price ($/MWh): | 0 | 10 | 0 | 46 |  |  |  | Check: should be 20% of capacity of base CCS facility | [7 empty] | 424.8107 | 412.6509 | 424.8107 | 424.8107
[7 empty] | Change in Revenues ($): | 0 | -2474.4773 | 0 | 2699.9498 |  |  |  |  | 62.96 | [5 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 192.7601
[11 empty] | 225.4726 | TOTAL CHANGE IN REVENUES | [9 empty] | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 19.1169
[14 empty] | Extra Generation Unit | [7 empty] | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 173.6431
[11 empty] | Check w/ Alternate Method |  |  | 100.3435 | Max Capacity (MW) | [6 empty] | Total Generation (MWh): | 314.8 | 263.254 | 314.8 | 507.5601
[11 empty] | Power Input to Store Lean Solvent (MW): | 64.0109 |  | 20.9664 | Ratio of generation at extra generating unit to generation at pumping unit (MW/MW) | [10 empty] | 1400.414 | Total Gen
[11 empty] | Energy Output When Discharge Lean Solvent (MW): | 242.2157
[11 empty] | Net Energy Delivered to Grid Decrease When Storing Lean Solvent (MW): | 247.4477
[11 empty] | Net Energy Delivered to Grid From Continuous Regeneration Decreased When Discharging Stored Lean Solvent (MW): | 183.5212
[11 empty] | Net Power Change (MW): | -188.7532

## NumericExampleV2MW450DiffTank
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  |  | 4 time steps:
t=0: max generation
Plant specification: CCS plant type on prior sheet, bituminous coal | [5 empty] | t=1: store lean solvent (fully charge lean solvent tank)
Plant Parameters w/ CCS | [5 empty] | t=2: max generation
Value | Ref to Prior Sheet (for reference) |  |  |  |  | t=3: max generation utilizing stored lean solvent
314.8 | 314.8 | MW | Net output
109.8 | 109.8 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  |  |  | t= | 0 | 1 | 2 | 3
5146 | 5146 | tons | Lean solvent flow rate |  |  |  | Non-flexible CCS
32.22 | 32.22 | MW | CO2 Capture System Use |  |  |  | Net Power Output to Grid (MW): | 314.8 | 314.8 | 314.8 | 314.8
77.58 | . | MW | Regenerator Use |  |  |  | Mass Solvent Continuously Regenerated (tons): | 5146 | 5146 | 5146 | 5146
0.021337 | 0.021337 | MWh/ton | Energy required per ton solvent regenerated |  |  |  | CO2 Capture System Power Use (MW): | 32.22 | 32.22 | 32.22 | 32.22
0.061174 | 0.061174 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  |  | Regenerator Power Use (MW): | 77.58 | 77.58 | 77.58 | 77.58
0.70656 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator |  |  |  | Total Power Input to Capture CO2 (MW): | 109.8 | 109.8 | 109.8 | 109.8
0.29344 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [7 empty] | 1259.2 | Total Net Power Delivery to Grid (MW):
9.7703 | 9.7703 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank
12.1196 | 12.1196 | ton/MWh | Continuous solvent flow per energy output to grid (net), CO2 capture system, and regenerator |  |  |  | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 314.8 | 191.0455 | 314.8 | 223.0394 | [Declines b/c of less continuous solvent regen] | 0
[7 empty] | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 121.1079 | [Based on discharged amount of stored lean solvent] | 415.4807
[7 empty] | Total Net Power Output to Grid (MW): | 314.8 | 191.0455 | 314.8 | 344.1473 | [Not at max net output because would need full lean solvent tank to get max; see right] | 415.4807
Plant Parameters w/ CCS Using Stored Lean Solvent | [6 empty] | Total Mass Solvent Continuously Regenerated (tons): | 5146 | 3646 | 5146 | 3646 | [Limited by absorber capacity] | 0
Value | Ref to Prior Sheet (for reference) | [5 empty] | Mass Solvent Continuously Regenerated for Net Grid Output (tons): | 5146 | 3123 | 5146 | 3646 |  | 0
415.4 | 415.4 | MW | Net output |  |  |  | Mass Solvent Continuously Regenerated for Fuel Input to Store Solvent (tons): | 0 | 523 | 0 | 0 | [Discharge entire tank] | 5146
5145 | 5145 | tons | Lean solvent flow rate |  |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 1500 | 0 | 0 | [Constrains stored lean discharged + solvent continuously regen'd] | 5146
3.825 | 3.825 | MW | CO2 Capture System Use |  |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 1500 |  | 5146
0 | . | MW | Regenerator Use |  |  |  | Mass of Solvent Passed Through Absorber (tons): | 5146 | 3646 | 5146 | 5146 |  | 0
1500 | . | tons | Lean and rich solvent tank size |  |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 1500 | 0 | 0 | 1500 |  | 0
1500 | . | tons | Initial mass of stored rich solvent |  |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 1500 | 1500 | 0 |  | 0
0 | . | tons | Initial mass of stored lean solvent |  |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 109.8 | 77.7946 | 109.8 | 77.7946 |  | 0
0.021337 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 32.22 | 22.8282 | 32.22 | 22.8282 |  | 0
0.080739 | 0.080739 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 77.58 | 54.9663 | 77.58 | 54.9663 |  | 0
3.784 | 3.784 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  |  | CO2 Capture System Power Use, Continuous Regen, for E to Store Lean Solvent (MW): | 0 | 3.2746 | 0 | 0
32.0054 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 32.0054 | 0 | 0 |  | 0
[7 empty] | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 9.3918 | 0 | 0 |  | 0
[7 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 22.6137 | 0 | 0 |  | 0
[7 empty] | CO2 Capture System Power Use, Total (MW): | 32.22 | 32.22 | 32.22 | 22.8282 |  | 0
[7 empty] | Regenerator Power Use, Total (MW): | 77.58 | 77.58 | 77.58 | 54.9663
[7 empty] | Total Power Input to Capture CO2 (MW): | 109.8 | 109.8 | 109.8 | 77.7946
|  |  |  | 3386 |  |  | Gross Power (CO2 capture sys, regenerator, net to grid) (MW): | 424.6 | 300.8455 | 424.6 | 421.9418
[7 empty] | Required Continuous Solvent for Gross Power Output (Not Applicable During Stored Solvent Discharge) (tons): | 5146 | 3646.1404 | 5146 | NA
[7 empty] | Required Adder to Continuous Lean Solvent (tons): | 0 | 0.14037 | 0 | NA
[11 empty] | 1164.7928 | Total Net Power Delivery to Grid (MW)
[11 empty] | -94.4072 | Change in Net Power Delivery to Grid
from Continuous Non-Flexible CCS Operation
[11 empty] | -8.105% | Change in Net Output as %
[7 empty] | Ratio of E to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.2586 | 0.25859 | 0.2586 | NA
[7 empty] | Ratio of E to CO2 Capture System to Continuously Regenerate Lean Solvent to Gross Power (E to Grid + CO2 Cap Sys + Regenerator) (MWh/MWh) (SHOULD BE CONSTANT): | 0.075883 | 0.07588 | 0.075883 | NA
[7 empty] | Ratio of E to CO2 Capture Sys to Continually Regenerate Solvent Used to Capture CO2 from E for Stored Lean Solvent to E to Capture Sys for Stored Lean Solvent (MWh/MWh): | NA | 0.34867 | NA | NA
[7 empty] | Diff in Net Pow Output from Continuous CCS Operations (MW:) | 0 | -123.7545 | 0 | 29.3473
[7 empty] | Price ($/MWh): | 0 | 10 | 0 | 42
[7 empty] | Change in Revenues ($): | 0 | -1237.5445 | 0 | 1232.5858
[11 empty] | -4.9587 | TOTAL CHANGE IN REVENUES
Check w/ Alternate Method
[11 empty] | Power Input to Store Lean Solvent (MW): | 32.0054
[11 empty] | Energy Output When Discharge Lean Solvent (MW): | 121.1079
[11 empty] | Net Energy Delivered to Grid Decrease When Storing Lean Solvent (MW): | 123.7545
[11 empty] | Net Energy Delivered to Grid From Continuous Regeneration Decreased When Discharging Stored Lean Solvent (MW): | 91.7606
[11 empty] | Net Power Change (MW): | -94.4072

## OLD DO NOT USE
PARAMETERS | [8 empty] | STEP 1 | [7 empty] | STEP 2 |  |  | STEP 3
[8 empty] | NORMAL OPERATION WITH CCS | [7 empty] | OPERATIONS USING STORED LEAN SOLVENT |  |  | RELATE NORMAL OPERATIONS TO OPERATIONS USING STORED LEAN SOLVENT
CCS SOLVENT | [7 empty] | Plant Parameters | [7 empty] | Plant Parameters |  |  | Volume of lean solvent stored equals volume of lean solvent later discharged.
Solvent Components | [7 empty] | 10 | Heat Rate, Gross (MMBtu/MWh) | [6 empty] | 10 | Heat Rate, Gross (MMBtu/MWh) |  | Normal operations tells us energy input per unit lean solvent stored.
| Molecular Weight (g/mol) | Density (g/cm^3) | [5 empty] | 11.1 | Heat Rate, Net (MMBtu/MWh) | [6 empty] | 10.11 | Heat Rate, Net (MMBtu/MWh) |  | Operations with stored lean solvent tells us energy output enabled per unit lean solvent discharged.
MEA | 61.08 | 1.01 | [5 empty] | 375 | Net Capacity (MW) |  |  |  |  | 119.5 |  | 494.5 | Net Capacity (MW)
Water | 18.0153 | 1 | [16 empty] | NORMAL OPERATIONS |  |  | STORED LEAN SOLVENT OPERATIONS
[8 empty] | GET VOLUME OF LEAN SOLVENT CIRCULATED TO | [7 empty] | GET VOLUME OF LEAN SOLVENT CIRCULATED TO |  |  | Vlean = a * Ecc |  |  | Vlean = b * Egrid
Solvent Composition (by weight) | [7 empty] | NET ENERGY DELIVERED TO GRID AT CONSTANT OUTPUT. | [7 empty] | NET ENERGY DELIVERED TO GRID USING CO2 EMISSIONS AS INTERMEDIARY.
70% | Water | [6 empty] | Assume operating at full output for 1 hour. | [7 empty] | Assume operating at full output for 1 hour. |  |  |  | a * Ecc = b * Egrid
30% | MEA | [18 empty] | Egrid / Ecc = a / b
[8 empty] | Get energy used in CO2 capture system | [7 empty] | 4999.395 | Gross Fuel Input (MMBtu) |  |  | 7.9899 | Egrid/Ecc | [MWh energy to grid/MWh energy to CO2 capture sys to store lean solvent]
Solvent Parameters | [7 empty] | 4162.5 | Gross Fuel Input (MMBtu) | [5 empty] | Egrid | 494.5 | Net Energy Output to Grid (MWh)
48.1606 | Molecular weight (g/mol) | [5 empty] | Egrid | 375 | Net Energy Output to Grid (MWh) | [9 empty] | CHECK
1.007 | Density (g/cm^3) | [7 empty] | Ecc/Egrid=HRPccs | [6 empty] | Get CO2 emissions from fuel input. |  |  | Above conversion factor from Egrid/Ecc should be less
[7 empty] | Ecc | 41.25 | Energy to CO2 Capture System (MWh) | [6 empty] | 1028375.5515 | CO2 emissions from input fuel (lb) |  | less than value for conversion factor from Egrid/Ecc
0.19 | Solvent loading factor (mol CO2/mol sorbent) | [14 empty] | 10599021.2033 | CO2 emissions from input fuel (mol) |  | during normal operations, since do not completely eliminate
[8 empty] | Relate volume of lean solvent (Vlean) to parasitic load of CCS system | [10 empty] | capture penalty when using stored lean solvent.
MISC. | [7 empty] | Vlean = a * Eccs = a * (Ecc + Eregen) | [7 empty] | Get required amount of lean solvent. |  |  | Ratio during normal operations:
205.7 | Fuel CO2 Content (lb/MMBtu) | Source: bituminous, EIA (http://www.eia.gov/tools/faqs/faq.cfm?id=73&t=11) | [5 empty] | Need total input to CCS system, which includes regenerator. | [7 empty] | 55784322.1225 | Moles lean solvent (mol) |  |  | 9.0909 | Egrid/Ecc
44.01 | Molecular Weight, CO2 (g/mol) | [6 empty] | Use IECM to get values for Vlean and (Ecc+Eregen) to calculate a (see below) | [6 empty] | Vlean | 2686605866.1688 | Mass lean solvent (g)
[8 empty] | 47.85 | a | [tons lean solvent / MWh energy to CO2 capture sys]
CO2 CAPTURE | [7 empty] | 43408802.25 | a | [g lean solvent / MWh energy to CO2 capture sys] | [5 empty] | Get relationship between Vlean & Egrid
11% | Heat Rate Penalty | [14 empty] | Vlean = b * Egrid
25% | Capacity Penalty | [14 empty] | 5432974.4513 | b | [g lean solvent / MWh energy to grid]
BASE PLANT (BEFORE CCS RETROFIT) | [19 empty] | ALTERNATE CALCULATION
10 | Heat Rate, Gross (MMBtu/MWh) | [6 empty] | IECM Data | [6 empty] | IECM Data |  |  |  |  | Mass CO2 to mass lean solvent conversion
500 | Gross Capacity (MW) | [6 empty] | Non-fuel-input-limited plants | [6 empty] | Fuel-input-limited plant, no CCS |  |  |  |  | MassCO2/MassLean = LeanLoading*MWCO2/MWLean
| Net MW? | [7 empty] | Ecc | Vlean |  | Eregen |  |  | 201.2 | Coal flow rate, plant w/out CCS (tons/hr) |  |  |  |  | [molCO2/molSolvent]*[gCO2/molCO2]/[gSolvent/molSolvent]
OPERATIONS WITH STORED LEAN SOLVENT | [7 empty] | Gross Output (MW) | CO2 Capture System Use (MW) | Mass lean solvent (tons) | Vlean/Ecc | Regenerator Use (MW) | Vlean/(Ecc+Eregen) |  | Plant w/ CCS |  |  |  |  | 0.17363 | gCO2/gSolvent
90% | Heat Rate Penalty Reduction | [6 empty] | 650 | 57.53 | 9158 | 159.1865 | 133.9 | 47.8399 |  | 535 | Gross output (MW) [adjusted so coal flow rate = above coal flow rate]
95.6% | Capacity Penalty Reduction | [6 empty] | 500 | 44.26 | 7045 | 159.1731 | 103 | 47.8406 |  | 201 | Coal flow rate (tons/hr) |  |  |  | Vlean/Egrid = NetHeatRate * CO2ContentFuel / [gCO2/gSolvent] = b
[8 empty] | 350 | 30.98 | 4932 | 159.1995 | 72.08 | 47.8556 |  | 48.18 | Ecc (CO2 capture system use (MW)) |  |  |  | 5432974.4513 | b | [g lean solvent / MWh energy to grid]
CONVERSION FACTOR | [10 empty] | 159.19 |  | 47.85 |  | 7870 | Vlean (mass lean solvent (tons)) |  |  |  | Same value as above - good.
453.592 | gram/lb | [13 empty] | 163.3458 | Vlean/Ecc
907185 | gram/short ton | (assumes IECM tons = short tons)
Values obtained from IECM using reference coal plant equipped with in-furnace NOx controls,
hot-side SCR, cold-side ESP, wet FGD, carbon injection (Hg control), and amine CCS system with 90%
CO2 capture. These CTs were included because plants retrofit in my fleet with CCS have them installed.
| HAIBO ADDITIONS | Calculations by Michael in italics | [5 empty] | Solvent mass values were obtained from Get Results -> CO2 Capture -> Diagram -> Sorbent Circ. (tons/hr)
|  | Fuel flow rate (tons/hr) | Gross MW | Net MW (delivered to GRID) | Electricity Use by CCS | Solvent Flow Rate (tons/hr) |  | CO2 capture system use values were obtained from Get Results -> Overall Plan t-> CO2 Capture System Use (MW)
| NSPS w/o CCS, including carbon injection for Hg | 201.2 | 650 | 608 | 0 |  |  | Non-fuel-input-limited plants were tested by simply changing gross output values of base plant in Set Parameters -> Base Plant -> Performance
| NSPS w/CCS, normal | 201.6 | 540 | 438.8 | 47.8 | 7608 |  | Fuel-input-limited plant was tested by setting up plant w/out CCS, getting coal flow rate value, then retrofitting
plant w/ CCS and adjusting gross output value until coal flow rates match.
| Capacity penalty |  | 16.92% | 27.83% |  |  |  |  | This matches how I am modeling CCS retrofits - assuming plants are fuel input limited, hence larger capacity penalty than efficiency penalty.
|  |  | Change in Net MW when retrofit CCS: | 169.2 | I.e., energy (in MWh) used to capture CO2 in 1 hour
|  |  | Solvent Flow Rate (tons) per Unit Energy (MWh) Used in CO2 Capture: | 44.9645 | tons/MWh
|  |  | Net Energy Delivered to Grid (MWh) per Unit Energy Used in CO2 Capture (MWh): | 2.5934 | MWh/MWh
| NSPS w/CCS, stored lean solvent | 201.2 | 650 | 583.8 | 5.98 | 7594
| Capacity penalty |  | 0% | 3.98%
|  |  | Solvent flow rate w/ stored lean solvent ~= solvent flow rate w/ continuous CCS | [5 empty] | T&S Config, CO2 Unit Comprresion Energy | [5 empty] | With default values:
| Net Energy Delivered to Grid Using Stored Lean Solvent (MWh) per Unit Stored Lean Solvent Used (tons): |  |  | 0.076876 | MWh/tons |  |  |  | 8.4 |  |  | CO2 Capture System Use |  |  | CO2 Capture System Use
| Above ratio of energy used in CO2 capture (MWh) to solvent flow rate (tons) tells me how much energy I need to put in for each ton of stored lean solvent. So I can use that value to convert the ratio in the above row from [Net MWh to grid using stored lean solvent/ton discharged stored lean solvent] to [Net MWh to grid using stored lean solvent/MWh Used in CO2 capture system to get that ton lean solvent]. That lets me relate energy I input during "charging" cycle (i.e., when storing lean solvent) to energy I later produce with that same volume of lean solvent. | [7 empty] | Capture, Regen. Heat Requirement |  |  | 4.55 |  |  | 46.53
| Net Energy Delivered to Grid Using Stored Lean Solvent (MWh) per Energy (MWh) Put Into CO2 Capture System to get 1 ton of Stored Lean Solvent: |  |  | 3.4567 | MWh/MWh |  |  |  | 0.01
Performance, Amine Scrubber Power Req
| Inreased Power Output with Stored Lean-Solvent Operation, compared tonormal CCS operation | [7 empty] | 0.7
| [Inreased MW] |  |  |  | 145
| [increased MW]/[MW power use by CCS in normal operation] |  |  |  | 3.0335 | [Problem w/ this value: does not include energy used in regenerator, which I need to capture. The increased power output in the denominator implicitly includes the benefit of eliminating demand in the regenerator, but the denominator does not include that term, biasing these results upwards.]
Note on X12: Haibo Zhai: is a funtion of plant heat rate? Repeat the calcuatins for subcritical and USC plants in the IECM
Note on R13: Haibo Zhai: almost same as the plant gross power output? Something wrong.
Note on A14: Haibo Zhai: this is wrong. 30% is on the mass basis instead of the mole basis.
Note on R20: Haibo Zhai: In normal operation, 90% is captured
Note on R21: Haibo Zhai: this is wrong!
Note on A25: Haibo Zhai: how did you get this? Not 27.8%
Note on B25: Haibo Zhag gross vs net power outputs?
Note on A28: Haibo Zhai: how did you get this number?
Note on M31: Haibo Zhai: is a function of net plante efficiency/heat rate?
Note on O31: Haibo Zhai: is a function of net plante efficiency/heat rate?
Note on B32: Haibo Zhai: compared to the plant without CCS?
Note on B33: Haibo Zhai: net power output!
Note on F60: Haibo Zhai: a function of plant size, net heat rate, coal rank?

## NumericExample_OLD
This is a numeric example to compare power generation over time for a non-flexible and flexible CCS plant. |  |  |  | 4 time steps: | [9 empty] | Same Example Using My Modeling Scheme
[5 empty] | t=0: max generation | [8 empty] | Base CCS Plant
Plant specification: CCS plant type on prior sheet, bituminous coal |  |  |  |  | t=1: store lean solvent (fully charge lean solvent tank) | [8 empty] | 455 | Max Capacity (MW) |  |  | **Note that these values ARE not the same as numeric value to left because of different storage amounts.
Plant Parameters w/ CCS |  |  |  |  | t=2: max generation | [8 empty] | 613.7 | Pre-CCS Capacity (MW) |  |  | **However, if you scale based on energy to continuous solvent regeneration, results are the same.
Value | Ref to Prior Sheet (for reference) |  |  |  | t=3: max generation utilizing stored lean solvent | [8 empty] | 11% | Heat Rate Penalty |  |  |  | t= | 0 | 1 | 2 | 3
455 | 455 | MW | Net output | [10 empty] | 25.86% | CCS Capacity Penalty |  |  |  | Continuous Gen
158.7 | 158.7 | MW | Net output decrease w/ CCS retrofit (i.e., energy to CO2 capture system + regenerator) |  |  | t= | 0 | 1 | 2 | 3 |  |  |  | 14.86% | Regenerator Capacity Penalty |  |  |  | Net Energy Output to Grid (MWh): | 455 | 455 | 455 | 455
7431 | 7431 | tons | Lean solvent flow rate |  |  | Non-flexible CCS | [7 empty] | 46.53 | Max Energy Input to CO2 Capture System (MWh) | [7 empty] | 1820 | Total Gen
46.53 | 46.53 | MW | CO2 Capture System Use |  |  | Net Power Output to Grid (MW): | 455 | 455 | 455 | 455 |  |  |  | 9.7786 | Net Energy to Grid per Energy Input to CO2 Capture System (MWh/MWh) |  |  |  | Use of Stored Solvent, True Pump System
112.17 | . | MW | Regenerator Use |  |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 7431 | 7431 | 7431 |  |  |  | 20% | Min loading of steam turbine |  |  |  | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 95.0541
0.021356 | 0.021356 | MWh/ton | Energy required per ton solvent regenerated |  |  | CO2 Capture System Power Use (MW): | 46.53 | 46.53 | 46.53 | 46.53 |  |  |  | 91 | Min load of steam turbine (MW) |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 37.224 | 0 | 0
0.06123 | 0.06123 | MWh/ton | Net energy delivered to grid per ton solvent regenerated |  |  | Regenerator Power Use (MW): | 112.17 | 112.17 | 112.17 | 112.17 |  |  |  | 159.7034 | Tons lean solvent regenerated per unit energy used in CO2 Capture System (tons/MWh) |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 9.306 | 46.53 | 9.7206
0.70681 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to regenerator |  |  | Total Power Input to Capture CO2 (MW): | 158.7 | 158.7 | 158.7 | 158.7 | [8 empty] | Solvent Regenerated (tons): | 7431 | 7431 | 7431 | 1552.4107
0.29319 | . | MWh/MWh | Share of total energy input to capture CO2 as energy input to CO2 capture system | [6 empty] | 1820 | Total Net Power Delivery to Grid (MW): | [7 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 481.6361
9.7786 | 9.7786 | MWh/MWh | Net energy output to grid per unit energy sent to CO2 capture system |  |  | Flexible CCS | [5 empty] | Hypothetical: full discharge of full lean solvent storage tank |  | Solvent Storage Generator |  |  |  |  | Solvent Flow from Stored Lean Solvent (tons): | 0 | 0 | 0 | 5951.1944
[6 empty] | Net Power Output to Grid from Continuous Lean Solvent Regeneration (MW): | 455 | 271.3101 | 455 | 271.3101 | [Declines b/c of less continuous solvent regen] | 0 |  | General Parameters |  |  |  |  | Percent of Continual Solvent Flow Displaced by Stored Solvent (%): | 0 | 0 | 0 | 80.09%
Plant Parameters w/ CCS Using Stored Lean Solvent | [5 empty] | Net Power Output to Grid from Discharged Stored Lean Solvent (MW): | 0 | 0 | 0 | 242.793 | [Based on discharged amount of stored lean solvent] | 601.3983 |  | 90% | Heat Rate Penalty Reduction |  |  |  | Total Max Capacity, Accounting for % Continual Regeneration Displaced (MW): | 0 | 0 | 0 | 576.6902
Value | Ref to Prior Sheet (for reference) |  |  |  |  | Total Net Power Output to Grid (MW): | 455 | 271.3101 | 455 | 514.1031 | [Not at max net output because would need full lean solvent tank to get max; see right] | 601.3983 |  | 95.75% | Capacity Penalty Reduction |  |  |  | Total Solvent Flow Rate (tons): | 7431 | 7431 | 7431 | 7503.6051
601.4 | 601.4 | MW | Net output |  |  | Mass Solvent Continuously Regenerated (tons): | 7431 | 4431 | 7431 | 4431 | [Limited by absorber capacity] | 0 |  | 3.7895 | Net energy output to grid per energy pumped (MWh/MWh) |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 37.224
7431 | 7431 | tons | Lean solvent flow rate |  |  | Mass of Lean-Solvent-to-be-Stored Regenerated (tons): | 0 | 3000 | 0 | 0 |  | 0 |  |  | [Includes energy to regenerator in denominator] |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 444.4121
4.55 | 4.55 | MW | CO2 Capture System Use |  |  | Mass of Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 3000 | [Discharge entire tank] | 7431 |  | 12.9389 | Net energy output to grid per energy pumped, excluding energy to regenerator in value this is multiplied with (MWh/MWh) |  |  |  | Total Net Generation (MWh): | 455 | 91 | 455 | 576.6902
0 | . | MW | Regenerator Use |  |  | Mass of Solvent Passed Through Absorber (tons): | 7431 | 4431 | 7431 | 7431 | [Constrains stored lean discharged + solvent continuously regen'd] | 7431 |  |  | equals prior parameter*(1+Eregen/Eco2capturesystem) | [7 empty] | 1577.6902 | Total Gen
3000 | . | tons | Lean and rich solvent tank size |  |  | Mass of Stored Rich Solvent at End of Period (tons): | 3000 | 0 | 0 | 3000 |  | 7431 |  | 606.9493 | Max total (Base + SS) achievable capcaity (MW) |  |  |  | Use of Stored Solvent, Incremental Pump System
3000 | . | tons | Initial mass of stored rich solvent |  |  | Mass of Stored Lean Solvent at End of Period (tons): | 0 | 3000 | 3000 | 0 |  | 0 | [6 empty] | Net Energy Output to Grid (MWh): | 455 | 91 | 455 | 455 | [same values as above b/c at base CCS facility]
0 | . | tons | Initial mass of stored lean solvent |  |  | Total Power Input to Continuously Regenerate Solvent (MW): | 158.6964 | 94.6284 | 158.6964 | 94.6284 |  | 0 |  | I model solvent storage generator as additional stand-alone generator, w/ only incremental generation to base CCS facility. |  |  |  |  | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 9.319 | 0 | 0 | [smaller than above b/c using scaled-down pump system]
0.021356 | . | MWh/ton | Energy required per ton solvent regenerated (continuous or stored) |  |  | CO2 Capture System Power Use, Continuous Regeneration (MW): | 46.529 | 27.7446 | 46.529 | 27.7446 |  | 0 |  | But solvent storage generator really should replace generation from base CCS facility. |  |  |  |  | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 9.306 | 0 | 0 | [same as above b/c internal to base CCS facility]
0.080931 | 0.080931 | MWh/ton | Incremental net energy delivered to grid per ton stored lean solvent discharged. |  |  | Regenerator Power Use, Continuous Regeneration (MW): | 112.1675 | 66.8839 | 112.1675 | 66.8839 |  | 0 |  | When I have full pump load at my stand alone generator, need to inflate this value to scale from incremental pump system |  |  |  |  | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 120.5772 | [smaller than above b/c using scaled-down pump sys & only incremental gen from pump sys, not full degree of output]
3.7895 | 3.7895 | MWh/MWh | Incremental net energy delivered to grid per unit energy used to store lean solvent |  |  | Total Power Input to Regenerate Stored Lean Solvent (MW): | 0 | 64.068 | 0 | 0 |  | 0 |  | to true pump system. |  |  |  |  | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 9.319
64.068 | . | MWh | Energy required to fully charge lean solvent storage tank |  |  | CO2 Capture System Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 18.7844 | 0 | 0 |  | 0 |  | True Pump System |  |  |  |  | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 111.2582
[6 empty] | Regenerator Power Use, Stored Lean Solvent Regeneration (MW): | 0 | 45.2836 | 0 | 0 |  | 0 |  | 37.224 | Max Capacity (MW) |  | [Excludes energy to regenerator] |  | Total Net Generation (MWh): | 455 | 91 | 455 | 575.5772 | [same value in hour 3 as above as intended]
[6 empty] | CO2 Capture System Power Use, Total (MW): | 46.529 | 46.529 | 46.529 | 27.7446 |  | 0 | 4.082 |  | [Steam turbine min load defined as 20%, so must | [7 empty] | 1576.5772 | Total Gen
[6 empty] | Regenerator Power Use, Total (MW): | 112.1675 | 112.1675 | 112.1675 | 66.8839 |  | 0 |  |  | maintain 20% load through continuous solvent regeneration.]
[6 empty] | Total Power Input to Capture CO2 (MW): | 158.6964 | 158.6964 | 158.6964 | 94.6284 |  | 0 |  | 7499.5898 | Tank size to meet max possible output using stored lean solvent (tons)
[6 empty] | Gross Power (MW): | 613.6964 | 430.0066 | 613.6964 | 608.7316 |  |  |  | 5944.8 | Solvent pumped at max pump capacity (tons)
[7 empty] | 0.25859 | 0.22006 | 0.25859 | 1695.4133 | Total Net Power Delivery to Grid (MW) |  |  |  |  | [Pump max capacity above does not include energy for regenerator.]
[10 empty] | -124.5867 | Change in Net Power Delivery to Grid |  |  |  |  | [~80% of tank size can be filled in 1 hour, which makes sense given 20% min load on ST.]
[11 empty] | from Continuous Non-Flexible CCS Operation |  |  | 79.27% | Percent of solvent necessary for max output that can be stored in 1 hour
[6 empty] | Diff in Net Pow Output from Continuous CCS Operations (MW:) | 0 | -183.6899 | 0 | 59.1031
[6 empty] | Price ($/MWh): | 0 | 10 | 0 | 40 |  |  |  | Incremental Pump System | [7 empty] | Use of Stored Solvent w/ Backcalculated Regenerator Energy Use
[6 empty] | Change in Revenues ($): | 0 | -1836.8987 | 0 | 2364.1252 |  |  |  | 151.9493 | Max incremental generation w/ stored lean solvent (MW) | [6 empty] | Net Energy Output to Grid (MWh): | 455 | 363.8729 | 455 | 455
[14 empty] | 1877.5166 | Volume of stored lean solvent for max inc. gen (tons) | [6 empty] | Pump Load / Energy to Store Lean Solvent (MWh): | 0 | 9.319 | 0 | 0 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[10 empty] | Check w/ Alternate Method |  |  |  | 40.0962 | Max capacity (MW), based on volume of stored lean solven | [6 empty] | Back-calculated Regenerator Energy Use to Store Lean Solvent (MWh): | 0 | 89.8722 | 0 | 0
[10 empty] | Power Input to Store Lean Solvent (MW): | 64.068 |  |  |  |  | necessary for max incremental gen above. | [5 empty] | Energy to Continuous Solvent Regeneration (MWh): | 46.53 | 37.211 | 46.53 | 46.53 | [This only captures pump / compression energy use (CO2 Capture System use in IECM), NOT regenerator energy use]
[10 empty] | Energy Output When Discharge Lean Solvent (MW): | 242.7882 |  |  |  |  | [Includes energy to regenerator.] | [5 empty] | Back-calculated Regenerator Energy Use for Continuous Regeneration (MWh): | 112.3402 | 89.8408 | 112.3402 | 112.3402
[10 empty] | Net Energy Delivered to Grid Decrease When Storing Lean Solvent (MW): | 183.6899 |  |  | 11.7563 | Max capacity (MW), excluding energy to regenerator. | [6 empty] | Tons Lean Solvent Stored (tons): | 0 | 4644.6523 | 0 | 0
[10 empty] | Net Energy Delivered to Grid From Continuous Regeneration Decreased When Discharging Stored Lean Solvent (MW): | 183.6899 |  |  | 9.319 | Max capacity (MW), excluding energy to regenerator and accounting for limit on how much true pump system can be filled in 1 hour. | [6 empty] | Tons Solvent Continuously Regenerated (tons): | 7439.1386 | 5949.2324 | 7439.1386 | 7439.1386
[10 empty] | Net Power Change (MW): | -124.5915 |  |  | 3.9944 | Ratio of pump max capacity in incremental vs. true system | [6 empty] | Tons Stored Lean Solvent Discharged (tons): | 0 | 0 | 0 | 4644.6523
[14 empty] | 39.06 | Reduction in base CCS net output per unit energy used to pump lean solvent for storage (MWh/MWh) | [6 empty] | Net Energy to Grid, Tons Continuously Regenerated (MWh): | 455.4985 | 364.2715 | 455.4985 | 455.4985
[14 empty] | 91.0003 | Max capacity of base CCS facility at max pump capacity (MW) | [6 empty] | Net Energy to Grid, Tons Stored Lean Discharged (MWh): | 0 | 0 | 0 | 375.8964 | 375.889
[15 empty] | Check: should be 20% of capacity of base CCS facility | [7 empty] | 613.8702 | 590.1159 | 613.8702 | 613.8702
[16 empty] | 91 | [5 empty] | Generation using Discharged Lean Solvent (MWh): | 0 | 0 | 0 | 375.889
[22 empty] | Generation from Pump Unit (MWh): | 0 | 0 | 0 | 37.224
[14 empty] | Extra Generation Unit | [7 empty] | Generation from Extra Generation Unit (MWh): | 0 | 0 | 0 | 338.665
[14 empty] | 142.6303 | Max Capacity (MW) | [6 empty] | Total Generation (MWh): | 455 | 354.5539 | 455 | 830.889
[14 empty] | 15.3053 | Ratio of generation at extra generating unit to generation at pumping unit (MW/MW) | [10 empty] | 2095.4429 | Total Gen